## Sheet1
Data Sheet - To be filled by the Vendor
Sr. No. | Description | Required - System Parameters | Offered - System Parameters
1 | Type of Chiller | Air Cooled Water Chiller
2 | Make & Model Name/Number of Chiller
3 | Cooling Capacity TR @ 42⁰C and 7/12⁰C Chilled Water In/Out | 17.55 TR
4 | Rated Power Input | Below 19.5 Kw
5 | EER Btu/h / W | 11.5
6 | COP @ 100% | Minimum 3.35
7 | Power Supply | 390-420V /3N/50 Hz
8 | Refrigerant | R-410a
9 | Factory Pre-Charge | Yes
10 | Water Flow | 11.2 m3/hr
11 | Water Pressure Drop | 44 kPa
12 | Noise Level at 1 Mtr distance | 66 db
Evaporator
1 | Type | Brazed Plate Heat Exchanger
2 | Material | Stainless Steel
3 | Chilled Water Flow | 11.2 m3/hr
4 | Pressure Drop | 6.4 psi
Condenser
1 | Condenser Type / Tube Material | Inner Groove Type / Copper
2 | Fins Material | Aluminum
3 | No of Rows | 3
4 | FPI | 16
5 | Fins Area | 3.43 m2
6 | Condenser Heat Exchange Area
7 | No. Of Tubes
Condenser Fan
1 | Type / Drive | Broad Wheel Axial Fan with Low Noise
2 | Quantity | 2
3 | Blade Material | Galvanized Steel
4 | Motor Poles | 6
5 | Air Volume | 12000 m3
6 | Fan Motor W | Below 950
7 | Fan Speed H/L RPM | 780/477
Compressor
1 | Type | High Efficient Hermatic Scroll
2 | Quantity per Chiller | 2
3 | Each Compressor Capacity | TR
4 | Compressor speed | RPM
5 | IP/Insulation Grade | IPX4/F
6 | Flow Control | EXV
7 | No of Refrigerant Circuits | 2
8 | In built Protection Devices | High Pressure Switch
9 |  | Low Pressure Switch
10 |  | Thermal Proctector
11 |  | Overload Protector
12 |  | Phase Sequencer
13 | External Wired Controller - | Chiller OEM make Common wired controller for all 3 Chillers by looping in comman communication cable
14 | Remote Operation | Remote Operation should be possible
15 | Diamensions in MM (LXWXH)
16 | Weight (Kg)
Pumps
1 | Make
2 | Type
3 | Model
4 | Type of fluid handled
5 | General Arrangement and Foundation Drawings | Kindly Attach
6 | Overall Size (including base frame) - L x D x H | mm x mm x mm
7 | Total Operating Weight | kgs.
8 | Duty Condition Selected - flow rate / head | USGPM/ MTRS
9 | Pump inlet / outlet connection dia | mm /mm
10 | Efficiency | %
11 | Pump performance curve and noise data | Attach
12 | Impeller dia | mm
13 | NPSH available | Meters
14 | Power Absorbed | KW
15 | Impeller dia | mm
16 | NPSH available | Meters
17 | Max impeller dia available for selected model
18 | Recommended motor KW | KW
19 | Selected Motor KW | KW
20 | Motor Make
21 | Motor Type | TEFC / Sq.Cage
22 | Motor Protection
23 | Class of Insulation
24 | Electrical Characteristics
25 | Starting Current | amps
26 | Full Load Current (Amps) | amps
27 | Motor Speed RPM | rpm
28 | Method of Starting | DOL / Star-delta
29 | Starter manufacturer
30 | Material of Construction for PUMP
31 | Casing
32 | Impeller
33 | Shaft
34 | Shaft Sleeve
35 | Gland Sealing
36 | Accessories included:
AHU
1 | Make
2 | Type
3 | Model
4 | Schematic & Dimensional Drawings | Kindlly Attach
5 | AHU Size L x D x H | mm x mm x mm
6 | Operating Weight | kgs.
7 | Type of Vibration isolators | Spring/
8 | Material of Construction of Components | Frame work / Casing
9 | Inner sheet casing thickness | mm
10 | Outer sheet casing | mm
11 | Thermal break | Provided/ Not Provided
12 | Insulation Material, Thickness & Density | Rockwool / mm / Kg/m3
13 | Drain pan material, gauge, insulation | / G/ PUF
14 | Make of fan
15 | Type of fan | Backward curved/Aerofoil
16 | Size and Dia of Fans | mm
17 | No. of Fans / AHU | Nos.
18 | Operating CFM & Range of CFM | CFM
19 | Fan Selection for Total Static Pressure | mm of .w.c.
20 | Fan RPM | RPM
21 | Fan Efficiency | %
22 | Fan Performance and Noise Curves | Attach
23 | AHU Outlet Velocity | FPM
24 | Type of Bearing
25 | Noise Level at 1Mtr from AHU | dBA
26 | Fan IKW | KW
27 | Recommended motor KW | KW
28 | Motor Make | SIEMENS/ABB
29 | Motor Type | TEFC / Sq.Cage
30 | Motor Effiicency | IE3
31 | Class of Insulation | F
32 | Electrical Characteristics
33 | Starting Current | amps
34 | Full Load Current (Amps) | amps
35 | Motor Speed RPM | rpm
36 | Method of Starting | DOL / Star-delta
37 | Starter manufacturer | L&T/ Siemens
38 | Water inlet / outlet temp to / from coil | Deg C
39 | Coil ADP | Deg C
40 | Coil capacity, TH | Btu/hr
41 | Coil capacity, SH | Btu/hr
42 | Coil capacity, LH | Btu/hr
43 | Coil Area, No. of Rows deep, Fin Spacing | Sq.Ft./ Nos / FPI
44 | Coil Face Velocity Air side | < 500 fpm
45 | Coil Flow Rate | USGPM
46 | Air pressure drop across coil | mm of w.c.
47 | Water pressure drop across coil | mm of w.c.
48 | Material of tubes / fins | Cu. / Al.
49 | Dia. of tubes / gauge of tubes
50 | Pre Filters Type, Face Areas | SQM
51 | Filters Ratings: Prefilter Efficiency | 90% down to 10 microns (G4)
52 | Filters Ratings: FineFilter Efficiency | 99.9 % down to 5 microns (F9)
53 | Filter make
54 | Conforming Standards
55 | Microprocessor Controller
56 | CFM
Electrical Work :
1 | Panel Manufacturer/Make
2 | Name of Electrical Contractor
3 | Electrical Contractor's Licence No. and Validity Period/Date (Attach Copy)
4 | IP
Evaporating Cooling System
1 | Make
2 | Type
3 | Model
4 | Schematic & Dimensional Drawings | Kindlly Attach
5 | Unit Size L x D x H | mm x mm x mm
6 | Operating Weight | kgs.
7 | Type of Vibration isolators
8 | Material of Construction of Components | Frame work / Casing
9 | Inner sheet casing thickness | mm
10 | Outer sheet casing | mm
11 | Insulation Material, Thickness & Density | Rockwool / mm / Kg/m3
12 | Make of fan
13 | Type of fan | Backward curved/Aerofoil
14 | Size and Dia of Fans | mm
15 | No. of Fans / Unit | Nos.
16 | Operating CFM & Range of CFM | CFM
17 | Fan Selection for Total Static Pressure | mm of .w.c.
18 | Fan RPM | RPM
19 | Fan Efficiency | %
20 | Fan Performance and Noise Curves | Attach
21 | Unit Outlet Velocity | FPM
22 | Type of Bearing
23 | Noise Level at 1Mtr from Unit | dBA
24 | Fan IKW | KW
25 | Recommended motor KW | KW
26 | Motor Make | SIEMENS/ABB
27 | Motor Type | TEFC / Sq.Cage
28 | Motor Effiicency | IE3
29 | Class of Insulation | F
30 | Electrical Characteristics
31 | Starting Current | amps
32 | Full Load Current (Amps) | amps
33 | Motor Speed RPM | rpm
34 | Method of Starting | DOL / Star-delta
35 | Starter manufacturer | L&T/ Siemens
36 | Water inlet / outlet temp to / from Unit | Deg C
37 | Air pressure drop across adiabatic heat exchanger section | mm of w.c.
38 | Air pressure drop across sensible heat exchanger section | mm of w.c.
39 | Adiabatic heat exchanger details
40 | Sensible heat exchanger details
41 | Water Sump construction details
42 | Pre Filters Type, Face Areas | SQM
43 | Filters Ratings: Prefilter Efficiency | 90% down to 10 microns (G4)
44 | Filters Ratings: FineFilter Efficiency | 99.9 % down to 5 microns (F9)
45 | Filter make
46 | Temperature Sensors, Relative Humidity Sensors & Water Level Sensors | Provided
47 | Water Re-circulation Pump details