Tender for

SUPPLY, INSTALLATION AND COMMISSIONING  OF UPS SYSTEM

at

Inter-University Centre for

Astronomy and Astrophysics

# Post Bag -4, Ganeshkhind, Savitribai Phule Pune University Campus, Pune 411 007.

Bill of Quantities (BOQ)

Financial Bid - Part  B

For “SUPPLY, INSTALLATION AND COMMISSIONING OF UPS SYSTEM ”

AT

INTER UNIVERSITY CENTER FOR ASTRONOMY & ASTROPHYSICS (IUCAA)

POST BAG 4, GANESHKHIND, SAVITRIBAI PHULE PUNE UNIVERSITY CAMPUS,

PUNE 411 007, INDIA

Name of Work  :   SUPPLY,  INSTALLATION  AND COMMISSIONING UPS SYSTEM AT IUCAA

A.	Name of Vendor  / Firm / Company	____________________________

____________________________

Postal Address				____________________________

____________________________

Telephone Off.			____________________________

Telex / Fax				____________________________

Email ID				____________________________

Signature & seal of

Bidder

| Supply, Installation, Testing & Commissioning of 150 KVA & Scalable upto 200 KVA MODULAR UPS SYSTEM |
| --- |
| Sr. No. | Description | Unit | Qty | Unit Rate | Amount |
|  | MODULAR UPS : |  |  |  |  |
| 1) | Supply, Installation, Testing & Commissioning of 150 KVA & Scalable upto 200 KVA, 3 Phase Input 3 Phase Output Modular UPS system with True ON Line Double Conversion technology & High AC - AC Efficiency of 95.5 %, Low Input Current Harmonic Distortion of < 3 % and Input Power Factor of > 0.99. The UPS shall utilize a single rack-mounted N+1 redundant, scalable and modular architecture as per mentioned specifications and consisting of the following - | Set | 1 |  |  |
| i) | Plug in & Hot Swappable power modules with integrated Controller and self-configuration power modules |  |  | INCLUSIVE | INCLUSIVE |
| ii) | Hot Swappable and full sized bypass in each module |  |  | INCLUSIVE | INCLUSIVE |
| iii) | In-built Manual Maintenance bypass |  |  | INCLUSIVE | INCLUSIVE |
| iv) | Reverse Phase Sequence Corrector kit (i.e. In the event of Phase sequence reversal at the input, UPS system shall continue shall to work on the main power supply without switching to Battery Mode) |  |  | INCLUSIVE | INCLUSIVE |
| v) | RS 485 Modbus protocol with each UPS module for BMS Connectivity alongwith SNMP. (Both should be simultaneously active) |  |  | INCLUSIVE | INCLUSIVE |
| vi) | Remote Alarm Monitoring (RAM) Module with each UPS and Cat 5 cable for RAM connectivity. |  |  | INCLUSIVE | INCLUSIVE |
| vii) | Day 1 Power Modules to support 150 KVA Load |  |  | INCLUSIVE | INCLUSIVE |
| viii) | The UPS System shall be subjected to load tests at factory before despatch & IUCAA site after installation in the presence of IUCAA`s representative with consultant. All consumables required during testing of UPS system at factory shall be included in the scope of UPS vendor. Also, client to arrange the required capacity Load for testing. The test shall be carried out as per technical specification & records to be submitted for approval. (The formats of all tests carried out at factory & at site with details of relevant standards as per latest standards & permissible limits should be submitted by UPS vendor for reference along with tender. All the arrangements of factory visit of IUCAA team including stay-if required, shall be in the scope of vendor.) |  |  | INCLUSIVE | INCLUSIVE |
| ix) | The power of the UPS system shall be scalable up to 200 KVA adding power modules with in Single Frame without disrupting load. |  |  | INCLUSIVE | INCLUSIVE |
|  | Batteries and MS Racks : |  |  |  |  |
| 2) | Supply, Installation, Testing & Commissioning of two Strings of SMF batteries with ten minutes backup time per string on 150 KVA Load with interconnectors, suitable MS battery Rack, flexible leads, terminations, connections between UPS & Batteries, etc. and all accessories. | Set | 1 |  |  |
| i) | External Battery Circuit breaker for each string mounted near Battery Rack |  |  | INCLUSIVE | INCLUSIVE |
| ii) | 3 Years warranty of batteries from the vendor |  |  | INCLUSIVE | INCLUSIVE |
| ii) | Interconnecting links between batteries, Battery cabling (uninyvin type) between Battery, DC Breaker & UPS of suitable size of 40 mtrs length |  |  | INCLUSIVE | INCLUSIVE |
|  | Isolation Transformer : |  |  |  |  |
| 3) | Supply, Installation, Testing & Commissioning of Delta Star Isolation Transformer of minimum 200 KVA capacity with necessary enclosures and accessories like cables & required rating Input & Output side switch gear with manual bypass switch & allied cabling, etc. & all the required accessories as per mentioned specifications. | Set | 1 |  |  |
| 4) | Dismantling & removal of old 3 X 40 KVA 'Magnaflux' UPS system with batteries & all accessories | Job Work |  |  |  |
| 5) | Buyback Offer - existing 3 X 40 KVA, Magnaflux make UPS system with Quanta make 12 Volt, 100 AH - 90 Nos. SMF batteries | Set |  |  |  |
|  | Total Amount - (A) |  |  |  |  |
| 6) | UPS Annual Maintenance Contract after Warranty Period : |
| Sr. No. | Year | Comprehensive AMC Costs in Rs. |
| 6.1 | First Year |  |
| 6.2 | Second Year |  |
| 6.3 | Third Year |  |
| 6.4 | Fourth Year |  |
| 6.5 | Fifth Year |  |
|  | Total Amount - (B) |  |
| 7) | Lowest Cost Criteria : |
| Sr. No. | Particulars | Rs. |
| 7.1 | SITC of UPS, Batteries & Allied Work (BOQ Item Sr. No. 1 to 5) - Total Amount - (A) |  |
| 7.2 | Cost of UPS Comprehensive AMC for 5 years after warranty period - Total Amount - (B) |  |
| Net Total Amount for Lowest Cost Criteria - |  |

In Words - Rs. ___________________________________________________

Sign & Seal of  Bidder