Tender for

TENDER FOR SUPPLY, INSTALLATION AND COMMISSIONING OF UPS SYSTEM

At

INTER – UNIVERSITY CENTRE FOR ASTRONOMY AND ASTROPHYSICS

POST BAG.4, GANESHKHIND, SAVITRIBAI PHULE

PUNE UNIVERSITY CAMPUS,  PUNE - 411 007.

Tel.  (020) 25604100 / 25691414, Fax: (020) 25604699

Technical Bid – Part- A

TENDER FOR SUPPLY, INSTALLATION AND COMMISSIONING OF UPS SYSTEM

INTER-UNIVERSITY CENTRE FOR ASTRONOMY & ASTROPHYSICS (IUCAA)

POST BAG 4, GANESHKHIND, SAVITRIBAI PHULE PUNE UNIVERSITY CAMPUS,

PUNE 411 007, INDIA

Name of Work : Supply, Installation & Commissioning of Modular UPS System at IUCAA, Pune.

A.	Name of Vendor / Firm / Company		____________________________

____________________________

Postal Address					____________________________

____________________________

Telephone Off.	         			            ____________________________

Telex / Fax					____________________________

Email ID					____________________________

Signature & Seal of Bidder

INDEX

| SR. NO. | CONTENTS | PAGE NO. |
| --- | --- | --- |
| 01 | Index | 3 |
| 02 | Tender Information | 4-5 |
| 03 | Technical Bid Form | 6-8 |
| 04 | Notice for inviting tender (NIT) | 9-10 |
| 05 | Appendix Form of Tender | 11 |
| 06 | General Terms & Conditions | 12-44 |
| 07 | Technical Specifications | 45-60 |
| 08 | List of Approved Makes | 61 |
| 09 | Undertaking Form - I | 62 |
| 10 | Declaration Form -II | 63 |
| 11 | EMD Refund request form- III | 64 |

TENDER  INFORMATION

Inter-University Centre for Astronomy and Astrophysics (IUCAA), Post Bag 4, Ganeshkhind, Savitribai Phule Pune University Campus, Pune 411007, invites sealed tenders in two bid format i.e  “Technical and Financial Bid”  from eligible and qualified tenderers for “Supply, Installation and Commissioning of UPS System" at IUCAA,  Pune 411007.

Date of sale of tender enquiry document	:  From 03/08/2015 to 05/08/2015 during 								   	 11:30 hrs to 15:30 hrs.

Place of sale of tender enquiry documents	:  Cashier’s office, IUCAA

Submission of questionnaire for Pre-Bid	:  11/08/2015 up to 1700 hrs

Pre Bid Meeting				:  12/08/2015 at 11:00 hrs.

Closing date & time for receipt of tender	:  08/09/2015 at 15:00 hrs.

Tender opening date & time			:  08/09/2015 at 15:30 hrs.

Place of tender opening			:  IUCAA’s office

Earnest Money Deposit	                        : Rs. 1,00,000/- (Rs. One Lakh only)

- Tender enquiry documents may be purchased on payment of a non-refundable fee of Rs. 2,000/-  (Rupees Two Thousand Only) per set in the form of cash or an account payee demand draft drawn on a Nationalised Bank, in favour of Inter-University Centre for Astronomy and Astrophysics (IUCAA) payable at Pune. Tender fees will be waived in case of firms registered under National Small Industries Corporation (NSIC)

- Tenderers shall ensure that their tenders, complete in all respects, are dropped in the tender box located at the address given above on or before the closing date and time indicated as above, failing which the tenders will be treated as late and rejected.

- EMD should be attached along with the technical bid only. The Demand draft for EMD should  be  drawn on Nationalized bank only  in favour of  “ IUCAA” payable at Pune. Demand draft from other banks will not be accepted and the tender will be summarily rejected.

- In the event of any of the above mentioned dates being declared as a holiday / closed day for IUCAA, the tenders will be sold/received/opened on the next working day at the appointed time.

- The tender documents are not transferable. Tender document without EMD shall be summarily  rejected. Envelope - 1 should contain (Part –I) the "Technical Bid" & "Earnest Money Deposit" the said envelope shall be  sealed and marked as “Technical Bid". Envelope - 2 should contain "Financial Bid ". The said envelope shall be marked as "Financial Bid." In case of any correction/addition/ alteration/ omission in original tender document shall be treated as non - responsive and shall be summarily rejected.

- The Administrative Officer (Purchase), IUCAA, Pune - 411007 on behalf of IUCAA reserves the  right to postpone the date of opening of tender without assigning any reason.

- Tender in which any of the prescribed condition (s) is not fulfilled or any condition including that of conditional rebate is put forth by the vendors, shall be summarily rejected. However, the tenders with unconditional rebate will be acceptable.

- Tenders shall neither be issued nor accepted by post/courier.

- IUCAA reserves the right to reject any or all of the tenders without assigning any reasons.

Administrative Officer (Purchase)

Inter-University Centre for

Astronomy and Astrophysics,

Post Bag 4, Ganeshkhind,

Pune 411 007

Tel. (020) 25604100 / 25691414

Fax (020) 25604699

| Technical Bid Form |
| --- |
| Tender for Supply, Installation, Testing & Commissioning of 150 KVA & Scalable upto 200 KVA MODULAR UPS SYSTEM |
| Client : Inter-University Centre for Astronomy & Astrophysics, Pune |
| 1 | Bidder’s Name (Company Name) and Address |  |
| 2 | Telephone Nos. Mobile No. Fax Nos. E-mail |  |
| 3 | Contact Person Name Designation Mobile # E-mail |  |
| 4 | Shop Act License No. and Validity Period/Date (Attach Copy) |  |
| 5 | Authorised Dealership / Partnership Certificates with OEM (Attach Copy) |  |
| 6 | Consistent minimum 5 years OEM/dealership in one brand only (Attach certificate from Manufacturer) |  |
| 7 | Nature of Business & Establishment Year |  |
| 8 | Organizational Capability (staff strength) | Name Qualification Experience |
|  | i) Project Managers |  |
|  | ii) Supervisors |  |
|  | iii)Technicians |  |
| 9 | Financial Capacity over last 3 years (Turnover & Profit) Balance Sheet to be enclosed |  |
|  | Financial year 2011-12,2012-13,2013-14 |  |
| 10 | Provide following details of Two best jobs completed of similar nature (ie UPS installation work 120 KVA and above ) You may be required to arrange for inspections of at least two such projects) |  |
| a. | Name of the project |  |
|  | Consultant |  |
|  | Completion year |  |
|  | Value UPS capacity |  |
|  | Scope of work Project proposed for inspection Client contact details (Name with tele/fax & e-mail). |  |
| b. | Name of the project |  |
|  | Consultant |  |
|  | Completion year |  |
|  | Value UPS capacity |  |
|  | Scope of work Project proposed for inspection Client contact details (Name with tele/fax & e-mail). |  |
| 11 | Work in hand (provide details in following format - Attach additional sheets if required) |  |
| i | Name of the project |  |
|  | Consultant %age completed/status Completion time UPS capacity in KVA Value. |  |
| ii | Name of the project |  |
|  | Consultant %age completed/status Completion time UPS capacity in KVA Value. |  |
| iii | Name of the project |  |
|  | Consultant |  |
|  | %age completed/status Completion time UPS capacity in KVA Value. |  |
| 12 | Infrastructure / Equipments / Machinery details |  |
| 13 | Tax details : VAT No. Service Tax no. Professional Tax no. |  |
| 14 | PAN Details : PAN No. |  |
|  | Photocopy of PAN |  |
| 15 | Quality assurance |  |
| 16 | A brief enlistment of Consultants with whom your organization has worked |  |
| 17 | Solvency certificate from Nationalised bank for minimum worth Rs.25/- lacs ( issued after May 2015) |  |
| 18 | List any arbitration cases/ legal disputes on Current/ previous projects - Mention name of project, reason for dispute, party filing the suit and current status) |  |
| 19 | Accreditation to quality control and quality management (please attach certificate) |  |
| 20 | List any awards, recognitions on previously executed projects |  |
| 21 | Any other documentation relevant to Pre-qualification ( Vendors can modify the tables to create additional space for information if required) |  |
| 22 | Address of OEM's Sales, Service & repair Center at Pune |  |
|  | (Please specify whether marketing// distributing / servicing the products) |  |
| 23 | Response time from service centre should be maximum 2 hours after launching a complaint |  |
| 20 | Response time for required spare parts from service centre after launching a complaint |  |
| 21 | Attach list of customers supported from Pune office |  |
| 22 | Prepared and Submitted by (Name & Signature) |  |
| Notes - 1) The Inter-University Centre for Astronomy & Astrophysics, Pune reserves the right to accept or reject any or all quotations without assigning any reasons. 2) The offers from OEM or their authorised dealers only will be considered. The offers received from unauthorised dealers / firms will be rejected. 3) Every statement made in the pre-qualification format should be supported by documentary proof for consideration otherwise the tender is liable to be rejected. 4) Please support Work in hand and completed work information with copy of the Purchase/ Work order from the client. 5) The OEM must have a sales service, repair & spares parts store departments at Pune for providing effective and efficient services |

SUBJECT : NOTICE INVITING TENDER (NIT) For “SUPPLY,  INSTALLATION & COMMISSIONING  OF UPS SYSTEM AT IUCAA, PUNE”

1. Owner             : Inter-University Centre for Astronomy and Astrophysics,  Pune 411007

2. Description of work :  Supply, Installation, Testing & Commissioning of 150 KVA & Scalable upto

200 KVA MODULAR UPS SYSTEM  at IUCAA, Pune.

3.  Schedule of work -   Two months to coincide with the schedule and progress of other works counted

From the date of LOI/WO

4. Form of Contract  -    Item Rate

5. Bid Documents  -  General Conditions of contract, Technical specifications and the BOQ in hard copy

is being issued with this  tender documents.

6. Receipt of Bids :    Bids should be submitted in sealed envelope superscribed as “Technical Bid” &

“Financial Bid” separately for “ Supply,  Installation & Commissioning of  UPS  System  at  Pune - 411 007”  will be received up to 15:00 hrs on 08/09/2015  and the same  will be opened at 15:30 hrs on 08/09/2015.

7. Earnest Money Deposit / Security Deposit :

EMD of Rs. 1,00,000/-  in the form of DD in favour of IUCAA from a nationalized bank should be submitted along with the Technical  bid. The successful bidder can opt to adjust the EMD amount towards payment of Security Deposit.  SD will be 5% of the contract value. However, the balance amount of SD has to be deposited separately by DD.

8. Acceptance / Rejection of Tenders –

Tenders missing or with incorrect, inaccurate calculations or generally not complying with the conditions will be rejected. Vendors  must return back all documents issued to them as part of Tender documents. Each document must be stamped and signed as token of acceptance.  If the original documents are not returned, the bid shall be summarily rejected. The vendor must fill the “vendor checklist for tender submission”, attached as part of Instructions to vendors and submit it with the tender documents. Vendors should quote their rates with the totals both in figures & in words. The total of each page along with carried over figures of the previous page shall be given in ink and signed by the vendor. No blank space shall be left. No over writing or cutting will be accepted. In such cases the quote will be rejected without any other consideration. No alterations, amendments or modifications shall be made by the vendor the Notice Inviting Tenders, Instructions to the Vendors, Contract Form, Conditions of the Contract, Drawings and Specification and if any such alterations are made or any special conditions attached, the tender is liable to be rejected without reference to the vendor. The acceptance of a tender shall rest with the Owner or its authorized representative who does not bind itself to accept the lowest tender and reserves to itself the right to reject any or all the tenders received without assigning any reason(s) whatsoever. Non acceptance of any tender shall not make the Owner liable for compensation or damages.

At any time prior to the Tender submission date, the Owner may, for any reason, whether on its own initiative or in response to a clarification requested by a vendor amend the tender documents by an Addendum (The “Addendum”) or issue Clarification memo.

The Addendum as well as clarification memo will be notified in writing to all tenderers. Tenders shall promptly acknowledge receipt thereof to the same person at the same address. Only amendments and clarifications to the Tender Documents made through Addendum or clarification memo will form part of the Tender Document.

8. If you have any questions /clarifications etc. it should be sent to administrative officer purchase on email (purchase@iucaa.ernet.in)

This notice inviting tender will form part of the tender document and the agreement executed by the successful tenderer.

Please note that there is an emphasis on completion of all works by the scheduled date of completion with strict adherence to quality and safety norms.

For further information or clarifications, the tenderer may contact the undersigned or IUCAA.

Kind regards,

Administrative Officer (Purchase)

Inter-University Centre for

Astronomy and Astrophysics,

Post Bag 4, Ganeshkhind,

Pune 411 007

Tel. (020) 25604100 / 25691414

Fax (020) 25604699

APPENDIX TO FORM OF TENDER

SUMMARY OF COMMERCIAL TERMS:

( Please refer Conditions of Contract for detailed explanation of Commercial Terms )

Sr No.              Item                                                  Details

| 1 | Earnest Money |  | Rs. 1,00,000/- (Rupees One Lakh only) in the form of DD drawn on nationalized bank in favour of Inter- University Centre for Astronomy and Astrophysics payable at Pune in a separate sealed envelope. |
| --- | --- | --- | --- |
| 2 | Mobilisation Advance |  | NIL |
| 3 | Security Deposit |  | 5 % of Contract Value by Demand Draft within 10 days of issue of LOI / WO which will be converted into Retention Money. |
| 4 | Retention money against total works |  | Retention money will be 5% of the final bill amount. In case of short fall after adjusting Security Deposit, same will be recovered from the final bill. |
| 5 | Advance against Materials brought to site |  | IUCAA may pay only 50% secured advance against approved materials brought at site by contractor. |
| 6 | Time of Work Completion |  | Two Calendar Months from the date of LOI / WO. |
| 7 | Compensation for Delay / Liquidated Damages |  | Half percent of Contract Price per week of Delay subject to a ceiling of 5% of final Contract Price. |
| 8 | Maintenance / Defect Liability Period for total Works |  | 14 Months from the date of Completion of all Works and acceptance by Owner or Manufacturer’s warranty period whichever is more. |
| 9 | Interim Bills Periodicity |  | Only Three RA bills |
| 10 | Time within which payment of Interim Running bill to be made after Project Manager’s Certification |  | Project Manager’s certification within 14 days of receiving the correct Interim invoice. Payment by Owner within 14 days of the issue of certificate for payment by the Project Manager. |
| 11 | Time within which payment of Final bill to be made after Project Manager’s Certification |  | Project Manager’s certification within 30 days of receiving the correct Interim invoice. Payment by Owner within 45 days of the issue of certificate for payment by the Project Manager. |
| 12 | ESI, PF & other regulatory rules & laws. |  | Vendor to cover his workers & staff under ESI, & PF scheme and comply with local laws & statutes dealing with employment of persons Necessary reports to be submitted. |
| 13 | Workers accommodation |  | Vendor to make his own arrangements for accommodation of his workers & staff including site office, godown, storage yard, etc. outside site i.e. not with Owners premises. |
| 14 | All Inclusive Rates |  | Rates to be inclusive of all taxes & duties including LBT , works contract/ turn over tax, etc. till the completion of work. |
| 15 | Venue of Arbitration and Arbitrator |  | Pune. Sole Arbitrator i.e. The Director, Inter-University Centre For Astronomy and Astrophysics, Pune. |
| 16. | Jurisdiction of Courts |  | Pune |

General Conditions of Contract

DEFINITIONS:

In the contract (as herein after defined) the following words and expressions shall have meanings here by assigned to them, except where the context otherwise requires: (In alphabetical order)

  - Approved/Approval:  Approved/Approval shall mean approved/approval in writing

  - Approved Equal: Approved Equal shall mean an alternative product or service approved by the Project consultant being equivalent to that specified in the Contract Documents with prior approval of the Owner.

  - Project Execution Programme: ‘Execution Programme’ shall mean the programmed to be furnished by the Vendor along with the tender as prescribed in Notice Inviting Tender.

  - Contract: The Contract shall mean the agreement between the Owner and the Vendor for the proper execution and successful completion of the Work in accordance with the Contract Documents and further documents as may be expressly incorporated in the letter of intent/ acceptance.

  - Vendor/Bidder: The  Vendor/bidder shall mean the person or persons, firm, company or consortium whose tender has been accepted by the Owner and includes the vendors legal representatives, successors and persons assigned with prior approval of the Owner.

  - Vendors/ bidders  Representative:  The Vendors/bidders representative shall mean the person or party duly appointed by the vendor/bidder, act for and on its behalf on a day-to-day basis during the execution of the work and the project. The vendors  representative shall be considered a “key person” for purposes of the execution  of contract. The vendor shall provide an authority letter designating the vendors representative for the project.

  - Contract Documents: The contract  documents shall collectively mean the documents to be listed in the contract between the Owner and the vendor and all modifications thereof and additions thereto incorporated in and made to any of those documents during the term of the contract.

  - Contract Price:  Shall mean the total of price referred to in the contract documents for the vendor's performance of the work. The prices mentioned in the order are firm and not subject to any escalation for any reason whatsoever unless specifically agreed by us. The charges for delivery at site and installation complete and the freight, insurance, loading, unloading, packaging and all other applicable charges involved in delivery of finished and installed product at site is included in the rates and the same shall be the responsibility of the vendor. The total cost mentioned above shall cover cost of all equipment/ material, labor, wastage, transport of equipment/ materials to site, profit, custom clearance (if applicable), transit insurance (if applicable), installation, testing, commissioning and all incidentals complete. The bidder should quote their prices inclusive of all taxes & levies. No extra claim for taxes will be entertained. The total cost is also inclusive of any shop drawings preparation (till the same are approved by consultants), engineering and site visits during the execution. The contract is neither a fixed lump sum contract nor a piece work contract, but is an item rate contract to carry out the work  according to the actual measured quantities at the rates contained in the schedule of rates and probable quantities as provided in the priced bill of quantities with detailed specifications. Item rates quoted in the bid proposal will be firm until the end of the contract. The contract price shall not exceed the amount as indicated in the Letter of Intent/Purchase Order. Amounts in excess of this number, not approved in advance by the Owner’s Representative shall be at the vendor's expense. The vendor has to closely monitor the quantities and cost and obtain an approval from the Owner/Project Consultant well in advance for any change outside the scope of the work which would cause the cost of the work to exceed the contract price as indicated in the Letter of Intent. No escalation in prices shall be allowed for any reason whatsoever during the period of the project.

  - Consultant  : Shall mean any person or agency duly appointed by the Owner. Project consultants’ to act as ‘CONSULTANT’ to render consultancy services in any area/field of activity connected with and arising out of the contract under a separate agreement setting out the consultant(s) responsibilities and terms.

  - Defect (S) Liability Period: Defect(s) Liability Period shall be 14 months after Virtual   Completion and any period extended as a result of rectification of the Work/change orders, between the Virtual Completion and the Final Completion of the work, and during which period the vendor shall be bound to replace and/or rectify and make good all defective materials, equipment and/or workmanship which arise in the Works or come to notice subsequent to the virtual completion of  the works and prior to the final completion of the works without requiring the Owner to bear any additional charges what so ever.

  - Drawings: ‘Drawings’ means all drawings, details and sketches along with the technical information therein, furnished by the Project consultant/ Consultant to the vendor under the contract and any modifications of such drawings or such other drawings as may be from time to time be furnished or approved in writing by IUCAA. All shop drawings, samples, patterns, models, operation and maintenance manuals, Product data and other technical information of a like nature submitted by the vendor shall also be referred to as 'Drawings'.

  - Final Completion:  Final Completion will be deemed to have been achieved when at the end of the Defects Liability Period, all snags identified by the Project consultant have been remedied to the satisfaction of IUCAA, a final completion certificate has been issued by the project consultant when all the requirements of the contract have been met and complied with and when all the defective items of work and defects have been replaced and/or rectified and made good as directed by and to the satisfaction of the owner.

  - Force Majeure:  Force Majeure are risks due to riots (other than those among vendor's or its subcontractor’s/ supplier’s employees) and civil commotion (in so far as both these are uninsurable), war (whether declared or not), invasion, act of foreign enemies, hostilities, civil war, rebellion, act of terrorism insurrection, military or usurped power, an act of Government, an act of God, such as lightening, earth quake, unprecedented floods, tornado, and damage from aircraft etc.

  - Headings:  The headings in these General Conditions of Contract shall not be deemed to be part thereof or to be taken into consideration in the interpretation or construction thereof or of the Contract.

  - Letter of Intent : ‘Letter of Intent’ shall mean the document issued to the successful bidder by the Owner signifying the Owner’s in-principle intent to enter into the contract

  - Measurement Books: The “measurement books” shall mean the books maintained during the currency of the project to record all measurements qualifying for payment. The contractor shall maintain measurement books of all work done by them. The vendor shall get the measurement books verified by IUCAA authorities.

  - Nominated Sub Contractor: "Nominated Sub-Contractor" refers to those specialists, tradesmen and others, whose credentials as well as quotations are evaluated and approved by the owner and then nominated for executing special works or supplying special equipment or materials, for which provisional sums are included in the contracts.  Such agencies shall be deemed to have been employed by the Contractor.

  - Owner: The Owner shall mean “IUCAA”, and the term Owner includes successors, assigns and affiliates.

  - Owner’s Representative: Owner’s Representative shall mean an employee/consultant of the Owner duly authorised to represent the Owner at site.

  - Project:  Project shall mean the total execution of the work performed under this contract for the “Supply, Installation, Testing & Commissioning of 150 KVA & Scalable upto 200 KVA MODULAR UPS SYSTEM”.

  - Public Holiday: ‘Public Holiday’ shall mean any day, which is declared as a public holiday by the Government of India or the State Government.

  - Project Coordination Services: ‘Project Coordination Services’ refers to those services, which need to be carried out by the vendor  in coordinating its work with the other agencies working at the site as per instructions of the owner / Project consultant. Such services shall be at no extra cost to the owner and must be to the full satisfaction of IUCAA / Project consultant.

  - Project Consultant: The ‘Project Consultant’ mean any person /agency appointed by IUCAA as a project consultant. The Project consultant shall be authorized to represent and act on behalf of the owner on a day-to-day basis during all stages of the project. All communications, approvals and decisions to be taken in connection with the project consultant’s services shall be channeled through IUCAA.

  - Provisional Sum: Provisional sum shall mean a lump sum included in the tender documents representing the estimated value of the works for which details are not available at the time of issue of tender.

  - Records and Audits: ‘Records and Audits’ shall mean the books and records required to be maintained by the vendor  in such manner, so as to enable the Owner/ Project consultant  to carry out effective financial control.

  - Retention Money : ‘Retention Money’ shall have the same meaning as described to it in clause .

  - References and Cross-References To Clause and Sub-Clause Numbers : Unless specifically stated otherwise, all references and cross-references made to clause and sub-clause numbers in these General Conditions of Contract refer to the clauses and sub-clauses of the General Conditions of Contract itself.

  - Schedule of Rates : ‘Schedule of Rates’ shall refer to the rates forming the basis for the Contract Price, as provided in a schedule to the Contract.

  - Singular and Plural: Words in the singular also include the plural and vice versa where the context              requires.

  - Site: The Site shall mean the location “ IUCAA, Pune University Campus, Ganeshkhind, Pune”.

  - Specifications: "Specifications" means the technical specifications for the Work included in the Project consultant’s Drawings and the Electrical/Civil/MEP/ Other Works technical specifications, and any modification thereof or addition thereto.

  - Sub-Contractors: “Sub-contractors” shall mean the persons, firms, companies or agencies who after approval of the  Owner/ Owner’s Representative/ Project consultant , have entered into a direct Contract with the vendor  in respect of any part of the work and any later package of the project, and include the Sub-Contractors' legal representatives, successors and permitted assignee. The vendor shall have full responsibility for the actions and work of any sub-contractor whether contracted by the vendor to perform portions of the work or any later.

  - Tender: “Tender” shall mean the vendor  priced offer for execution and completion of work as per technical specifications mentioned in the tender documents and remedying any defects arising therein, in strict accordance with the contract documents as issued with the tender and as per the agreement signed by the vendor thereafter.

  - Tender Documents: “Tender Documents” shall mean the, Notice Inviting Tender, General Conditions Of Contract, Special Conditions Of Contract, Works Technical Specifications, Bill Of Quantities With Detailed Specifications, Environmental, Health & Safety (EHS) Plan, Preliminary Project Construction Schedule, Drawing – Site Location, Drawings Of Project consultant & M&E Services/ Works and  vendors Pro-forma of  Bank Guarantee for Performance Bond any other related documents.

  - Temporary Works: Temporary works mean all temporary works of every kind required for the execution of the Work by the Contractor.

  - Terms “and”, “or”, “and/or”: The terms “and, “or”, “and/or” used in context with the description or enumeration of two or more items or components of work of documentation or anything similar shall mean as is relevant and applicable to the text.

  - Tests on completion: Tests on completion shall mean all the system testing required to be done by the vendor, to the entire satisfaction of  IUCAA and IUCAA’s representative, prior to handing over the project.

  - Vendors: “Vendors” shall mean and include all suppliers, contractors, sub-contractors, nominated sub-contractors engaged for the Project.

  - Virtual Completion: Virtual completion will be deemed to have been achieved upon a Virtual Completion Certificate being issued by the Project Consultant, when the work, according to IUCAA and Project consultant, has been completed in every respect in conformity with the contract documents and are ready and fit for the intended purpose, complete with all systems and services having been tested and commissioned.

  - Written Notice: Written Notice shall be deemed to have been duly served if delivered in person to the authorized representative of the firm / company for whom it is intended, or if hand delivered at and a written delivery receipt obtained from such person or if sent through e-mail when confirmed through electronic mail (e-mail) as received by such person. In case where written notice is sent by fax or courier service or speed post with acknowledgement to the last business address known to the party who gives the notice it shall be deemed to have duly served when it is actually served upon the other party.

  - Works: “Works” shall mean and include all materials, plant and machinery, equipment and labour necessary to execute the Project in full compliance with the requirements of the contract document.

  - Working day:  A working day is defined as any day between Monday and Saturday, both inclusive, and excluding any Public Holiday as notified by the Government of India/State Government.

2. SCOPE, EXTENT, INTENT AND OTHERS

  - Scope: The general character and the scope of the work shall be as illustrated and defined in the  Drawings, Specifications, Schedule of Rates, BOQ and other Contract Documents.

2.2	Extent: The vendor shall carry out and complete the work under the contract in every respect, and work shall include the supply of all labour, equipment, materials, plant and machinery, tools, transportation, form work, scaffolding and all things necessary for the proper execution and successful completion of the Work in accordance with the contract documents to the directions and satisfaction of IUCAA / Project consultant. The  vendor shall be fully responsible and liable for all matters in connection with or arising out of or being a result or consequence of its carrying out or omitting to carry out any part of the work. Where any parts of the work may be executed by or through Sub-contractors, such responsibility and liability of the vendor shall cover and extend to the work of all such Sub-Contractors.

2.3 	Intent: The contract documents shall be binding on the vendor/ vendors Representatives/ Sub-Contractors as the case may be. Wherever it is mentioned in the contract documents that the vendor shall perform certain work or provide certain facilities and services, it is understood that the vendor shall do so at its own cost. Materials or work described in the contract documents which have a well known technical or trade meaning, shall be held to refer to such recognised standards as are applicable to them.

2.4 	Instructions of  Estate  Manager: The Project consultant may from time to time, through the Estate Manager, issue further supplementary drawings, written instructions, details, directions, and explanations, which shall be collectively referred to as the ‘Instructions of  IUCAA authorities. The vendor shall forthwith comply with and duly execute the work comprised in such Instructions of IUCAA authorities, provided always that verbal instructions, directions and explanations given to the vendor or vendors  representative by the Project consultant or IUCAA authorities shall, if involving a variation, be confirmed in writing immediately thereafter by IUCAA.

2.5 	Approval of Estate Manager: Approval of the Estate Manager shall always mean approval in writing. The onus shall be on the vendor  to obtain all the necessary approvals in writing. Such approvals, however, shall not relieve the vendor of any of its responsibilities under the Contract.

2.6 	Increases/Decreases to scope of Work: The Owner reserves the right to increase or decrease the scope of the work on any or all items or to change the nature of the work involved in any or all items or to completely delete any items of the work under the contract. The bidder shall not be entitled to claim for loss of anticipated profits, for mobilization of additional resources, or for any other such reason on account of these change orders. In the event that the owner elects in writing to add an item to scope of the project or to delete an item from its scope, the owner shall be entitled to increase/ reduce (as the case may be) an appropriate amount from the contract Price.

2.7  Items of work for completion:  The bidder is bound to carry out any items of work necessary for proper execution and completion of the work even though such items of work may not be expressly be described in the contract documents.

2.8 Access for Owner, Project consultant :  The owner, owner’s representative,  the project consultant, and their respective consultants shall at all times have access to the work and the site and to the workshops or other places of the contractor where the work is to be so executed and in workshops or other places of Sub-Contractors and suppliers. The bidder shall by a term in its Sub-Contracts so far as possible, secure a similar right of access to those workshops or places for the owner, owner’s representative, project consultant, and their respective consultants and shall do everything for the purposes of carrying out inspections to ascertain and ensure that work is being carried out in conformity with the contract documents or for any other purpose in connection with the work under the contract.

3. PROJECT CONSULTANT / OWNER’S REPRESENTATIVE, CONTRACTOR & CONTRACTOR’S REPRESENTATIVE: The status, duties and responsibilities of the Project Consultant / Owner’s Representative, and Bidder/ Bidders’s Representative shall be as detailed below:

3.1 Role and responsibilities of the IUCAA Estate Manager / Department

i. The Estate Manager shall be responsible for the day-to-day supervision, progress monitoring, co-ordination and direction of the project, and generally to ensure that the work is carried out in all respects in strict conformity with the contract documents and timelines.

ii. The Estate Manager shall have the authority to stop the work whenever such stoppage may be necessary to ensure the proper execution of the Project. The vendor shall provide all the necessary facilities to the Estate Manager in the performance of  his duties as a Estate Manager and shall comply with all instructions as may be issued by the Estate Manager. The vendor shall refer all matters relating to the performance of the contract to the Estate Manager. The vendor shall not be entitled to claim extensions, extra costs or losses in this regard.

iii. The Estate Manager shall observe sound and established engineering practices using latest standards, codes and regulations, as applicable for the purpose specified and suitable for respective uses intended. Supervision over the vendor shall be maintained by Estate Manager who shall exercise constant and continuous supervision and control over quality, workmanship and materials, plant, machinery, equipment etc. used for the project as and when may be required.

iv. Estate Manager will work in close co-operation and co-ordination with the project consultant for the execution of the project in accordance with the contract documents.

v. All communication by the vendor with the owner or the owner’s consultants shall be done through the Estate Manager.

3.2 Decisions: The Estate Manager in consultation with the Project consultant/ Consultant shall make decisions on all matters relating to the execution and progress of the Project, including the claims and queries of the vendor. The decision, opinion, direction and interpretation of the Estate Manager (in consultation with Owner and/ or Project consultant/ Consultant), with respect to any or all matters including the following matters shall be final and binding on the vendor, except for matters involving financial implications which shall be decided in consultation with and with the prior written approval of the owner. Notwithstanding the generality of the foregoing, unless stated to the contrary below, the decision of the Estate Manager in respect of the following actions shall be binding upon the vendor:

i.   Any discrepancy in the drawings and specifications;

ii.  The removal and/or re-execution of any work already executed by the vendor.

iii. The dismissal from the Site of any person employed upon the work by the vendor or the Sub-

Contractor.

iv. The opening up for inspection of any part of the work covered up.

v.  All materials and workmanship used by the vendor or the sub-contractors.

vi. Everything that must be provided or done by the contractor in order to properly executes and

successfully completes the work under the contract.

vii. Delay and extension of time involved in the execution of the works (only with prior approval of

Owner).

viii. Supervising the replacing and/ or rectifying and making good all defective items of work and during

the Defects Liability Period.

ix. Removal of any material/equipment/plant and machinery brought by the vendor to the site for

execution of the work.

3.3 Role and Responsibilities of the Vendor’s Representative:

i. The vendors’s representative shall represent the vendor at the Site. The vendor’s representative shall be on site at all times during performance of the work and the Project Coordination Services and shall be responsible for the day-to-day interaction with the Estate Managers.

ii. The vendor’s representative shall have adequate experience in handling similar kind of projects, competent enough and have the authority to make and communicate all decisions called for in this contract to be made by the vendor. The vendor’s representative may be required to produce appropriate documentation and referrals in respect of previous assignments. The vendor’s representative shall be responsible for the day-to-day supervision and oversight of the Project Coordination Services, including, without limitation, the EHS Plan implementation.

iii. The vendor shall submit to IUCAA the name and other details of the vendor’s representative within 7 days of execution of contract.

3.4 Vendor’s Responsibilities: The vendor shall have the following responsibilities in carrying out the work and the project coordination services.

i. The vendor shall, on the instruction of the Estate Manager, immediately dismiss from the work any person employed thereon by him who may, in the opinion of the Estate Manager, be incompetent or who engages in unlawful or disorderly conduct, and such persons shall not be re-employed on the work without the prior written permission of the Estate Manager.

ii. Vendor  shall indemnify the owner for loss suffered by the owner on account of any act/  omission/ neglect of the vendor's workers, employees and Sub-contractors etc.

iii.The vendor shall comply with all safety standards to the satisfaction of the owner’s  representative/ Estate Manager.

iv. The vendor shall take full responsibility for the management & supervision of the Sub-contractors and the Nominated Sub-Contractors and the vendor’s representative. The vendor shall act as an independent contractor in the performance of its obligations under the contract. The employees and the Sub-contractors utilised by the vendor shall not be construed as the owner’s employees and shall work under the control and management of the vendor who shall be solely responsible for their acts & related risk. The vendor shall be solely responsible for the payment of compensation and all statutory benefits of its employees and the employees shall be informed that they are not entitled to any of the owner’s employee benefits. The vendor and not the owner shall be solely responsible for deduction and/or payment of all statutory payments including without limitation, provident fund, ESI, MLWF, workers’ compensation, disability benefits and unemployment insurance or for withholding and paying employment taxes viz. Profession tax and Income tax etc for the employees. The employees and the sub-contractors shall affirm they are not employees of the owner for any purpose and that they shall not exercise any rights, seek or be entitled to any benefit accruing to the regular employees of the owner.

v. The vendor shall ensure that all sub-contractors engaged by it exercise such skill, care &  technical

competence to represent a high standard within their respective professions or trades as is appropriate

for the satisfactory execution of their work and services.

vi. The vendor shall exercise constant and continuous supervision and control over the workmanship,

materials, plant, machinery, equipment etc used in the work and report on the status of the same to the

owner’s representative and Estate Manager as and when required in terms of the contract.

vii. The vendor shall be responsible for obtaining all necessary permits, approvals, certificates and the

like and submit the same to the IUCAA Estate Manager prior to the commencement of the works.

viii. All the obligations and responsibilities of the vendor under the contract shall be duly fulfilled

subject to the satisfaction of the owner’s representative and IUCAA Estate Manager.

ix. Any activity conducted or responsibility assumed by the owner’s representative or IUCAA Estate

Manager shall not relieve the vendor of any of its obligations and responsibilities under the contract.

x. The vendor shall observe sound and established engineering practices in the execution and completion

of the  works in  accordance with the  contract.  The vendor  shall use  latest standards, codes and

regulation, as applicable for the purpose specified and suitable for respective uses intended.   The

vendor must keep at site the latest IS codes for quick referencing.

4.0 SITE:

4.1 Vendor to satisfy itself about site conditions: The vendor represents that before tendering for

the work, the vendor  has visited the site  and  satisfied  itself  about the site conditions for       construction and for logistics and smooth flow of workmen and materials as well as permission from       appropriate governmental authorities for this purpose. The vendor has examined the site and taken       note of the correct dimensions of the work, and facilities for obtaining any special articles called for   in the contract documents. The vendor has also made its own assessment and obtained all  information on the site constraints and on all matters that will affect the execution, continuation, progress, and completion of the works. Any extra claims made in consequence of any  misunderstanding, incorrect information on any of these points or on the grounds of insufficient description or information shall not be entertained or allowed at any stage

4.2 Access to site by the Vendor   : The access to the site will be given immediately on award of the

contract to the vendor and the site shall be shared with other vendors as applicable. The vendor shall upon being given such access commence the work and diligently proceed with the  execution of the work in accordance with the contract documents. Access to the site by the vendor shall be merely a license for carrying out the execution of the work under the contract, and the vendor shall not by his being allowed such entry on the site, acquire any right, lien or interest either in the work carried out by them under the contract or anything appurtenant or attached thereto or to any part of the site, and its claim will only be in the nature of money found due and payable to them in accordance with the payment certificates under the provisions contained herein. The work shall be free from all liens, charges and claims of whatsoever nature from any  party other than the owner. The owner shall have a lien over all work performed by the contractor,  Sub-Contractor and vendors and also for the materials and equipment brought on site by them.

5. TYPE OF CONTRACT:  The contract shall be an item rate contract only to execute the project according to the actual measured quantities, at the rates contained in the Schedule of Rates and        probable quantities as provided in the Priced Bill of Quantities with detailed specifications. The        vendor shall be entitled to payment, in Indian Rupees, of no more than the Contract Price as stated in the Letter of Intent, in consideration of the work performed and for the completion of the work to the satisfaction of the Owner/ Owner’s Representative. The vendor understands and agrees that the amount payable is assessed on a re-measurable basis in accordance with the tendered  rates.   However, the contract price may be altered on account of a change order issued in accordance with Clause hereto. The Contract Price shall include payment for the supply of all labour (including payment to the Sub-Contractors), equipment, materials, plant and machinery, tools,  transportation, framework, scaffolding, construction of civil works and shall also include all applicable taxes including the WCT, duties, LBT/octroi, levies, royalties, fees, insurance premiums, contributions towards employees benefits including ESI and PF and funds, provision and distribution of power and water and all services and activities constituting the Scope of Work defined in the General Conditions of Contract. The contract price shall also include the vendor's establishment, infrastructure, overheads and all other charges, and shall generally be inclusive of every cost and expense required by the contract to be borne by the vendor and necessary for the proper execution and successful completion of the work under the contract in conformity with the contract documents and the best engineering and construction practices and to the satisfaction of the Project consultant, IUCAA Estate Manager. No escalation of the prices shall be allowed during the period of the contract for any reasons whatsoever and the prices quoted by the vendor shall be deemed to be fixed and constant throughout the duration of the Project and Defects Liability Period.

6. TAXES, DUTIES ETC.:  The total cost mentioned above shall cover cost of all equipment/ material, labour, wastage, transport of equipment/ materials to site, profit, transit insurance (if applicable), installation, testing, commissioning and all incidentals complete, inclusive of all taxes and duties. However, any statutory variation shall be absorbed by you without any impact being passed onto the clients. The total cost is also inclusive of any shop drawings preparation (till the same are approved by consultants), engineering and site visits during the execution.

7. NOTICES, FEES, BYE-LAWS, REGULATIONS, ETC. :

The vendor shall comply with all applicable laws and government acts including the by-laws or regulations of local authorities relating to the work in so far as construction, fabrication and installation activities are concerned, and it shall obtain from the local authorities all permissions and approvals required for the playing of trucks, construction of machinery etc., and also for construction of temporary offices, stores and other temporary structures in connection with the work, and the vendor shall give all notices and pay all fees and charges that are and that can be demanded by law there under. In the contract price for the work, the vendor shall allow for such compliance and work, and for the giving of all such notices, and shall include the payment of all such fees and charges. However, no title or proprietary interest of any kind shall be created in favour of the vendor  by virtue of erection of the temporary structures.

8. LICENCES AND PERMITS:  The vendor shall directly obtain all licenses and permits for the materials under Government control, and those required to be obtained by the vendor for the execution of the Work. The vendor Price shall include all transportation charges and the other expenses that may be incurred in this connection.

9. ROYALTIES AND PATENT RIGHTS: All royalties or other sums payable by the vendor in respect of the supply and use of any patented articles, processes or inventions for the carrying out of the Work as described by or referred to in the contract documents, shall be deemed to have been included in the contract price. The vendor shall keep the owner indemnified against all such demands as may arise on account of payment of royalties.

10. INSURANCE: Before commencing the execution of the work, the vendor, without limiting his obligations and responsibilities under this contract shall insure in the joint names of the Vendor and Owner, against his liability for any material or physical damage, loss or injury which may occur to any property, including that of the Owner/ IUCAA Estate Manager / Project consultants, Sub-Contractors, Vendors or to any person including any employee of the Owner/ Estate Manager / Project consultant, Sub-Contractors, Vendors or a member of the general public, by or arising out of the execution of the Work or in carrying out the Contract. The vendor shall ensure that the Owner and Project Manager are named as an additional beneficiary in all such insurances obtained. The vendor shall provide a copy of such policy on or before the date of execution of the contract. The vendor shall insure against all such liabilities and shall continue such insurance during the currency of the contract including the Defects Liability period. Premium for all insurance policies shall be paid and borne by the Contractor and shall not be reimbursable. The vendor shall produce to IUCAA Estate Manager all certificates of insurance with in 7 (seven) days from the date of letter of intent/award. These certificates shall be fully executed and shall state that the policies cannot be cancelled until completion of the contract. The vendor shall obtain written confirmation of similar certificates from all sub-contractors and thereby assume responsibility for any claims or losses to the Owner resulting from failure of any of the sub-contractors to obtain adequate insurance protection in connection with their work and shall indemnify the Owner accordingly. It shall be obligatory for the vendor to obtain and retain for all relevant times the insurance cover (in the joint names of the Vendor and Owner) under the following policies:

10.1 Vendor's All Risk Insurance Policy to inter alia cover the following:

i.  The entire contract value (including the Contract Price plus 10% of the Contract Price for the period of

completion of the Works or any extended period.

ii.  Civil commotion, riots, war and other disturbances

iii. All Plant and machinery owned by the vendor for the project.

iv. Damage insurance against loss or damage by fire or any other disaster to the works.

10.2 Third Party Insurance Policy : The vendor shall take a third party insurance to cover for any damages to third party. This policy shall be effective up to the end of the project including any extensions granted and shall include any damage to the properties including surrounding and adjacent properties and/or injury including death to the persons of the general public and anyone else deemed to be third party subject to individual claims not exceeding Rs.2,00,000/-limited to a maximum sum of Rs.10 Lakhs.

10.3 Workman’s Compensation Policy :  Policy to cover vendor's liability under Workmen's Compensation Act 1923, Minimum Wages Act 1948, Contract Labour (Regulation and Abolition) Act 1970 and other relevant Acts listed elsewhere to cover the vendor liability under the applicable labour laws. This shall be for the period up to Final Completion of the Work. The vendor’s liability under this policy shall also include the Sub-contractors liability under the applicable labour laws.

10.4 Failure to insure:  If the vendor fails to comply with the terms of this clause, the Owner may effect the insurance and deduct the expenses from any moneys that may be or become payable to the vendor or may, at his option, refuse payment of any monies to the vendor until the vendor complies with this condition.

10.5 No limit to liability:  In addition to the liability imposed by law upon the vendor for injury (including death) to persons or damage to property by reason of the negligence of the vendor or his agents, which liability is not impaired or otherwise affected hereby, the contractor hereby assumes liability for and agrees to hold the Owner harmless and indemnifies him from every expense, liability, payment, claim by reason of any injury (including death) to persons or damage to property suffered on account of any act or omission on the part of the vendor, his employees, agents, servants, workmen, suppliers assigns or any of his sub-contractors, or any person directly or indirectly employed by any of them or from the conditions of the site or any part of the Site which under the control of the vendor or its employees or any of its sub-contractors, or any one directly or indirectly employed by either of them or arising in any way from the work.

11 VENDOR'S  SITE ORGANIZATION, INFRASTRUCTURE AND RESOURCES :

11.1Vendor’s representative and supervisory staff :

i. The vendor shall at its cost provide and ensure continued effective supervision of the work with the help of the vendor’s representative, assisted by full time qualified, experienced and competent engineers, supervisors, Safety officers, Safety stewards and adequate staff, to the satisfaction of the Owner’s Representative and the IUCAA Estate Manager for the entire duration of the work.

ii. The vendor shall submit its proposed site organization chart for the approval of the IUCAA Estate Manager.

iii. The vendor’s  representative shall be on the site at all times as the work and the project progresses and shall be responsible for carrying out the work to the true meaning of the Drawings, Specifications, Conditions of Contract, Schedule of Rates, the other Contract Documents, and instructions and directions of the Owner’s Representative and the IUCAA Estate Manager.

iv. The instructions and directions given in writing to the vendor’s representative or to any of its assistants at the site by the Owner’s Representative or the IUCAA Estate Manager shall be deemed to given to the vendor officially.  Attention is called to the importance of the vendor requesting written instruction from the Owner’s Representative or the IUCAA Estate Manager before undertaking any Work where the IUCAA Estate Manager's and/or Owner’s Representative direction or instructions  are required. Any such work done in advance of such instructions will be liable to be removed at the vendor's expense and will not be paid for unless specifically approved in writing by the IUCAA Estate Manager and/or Owner’s Representative, as the case may be. It shall be the vendor’s responsibility to provide written intimation to Owner’s Representative or the IUCAA Estate Manager, well in advance, all through the execution of the project, if the work is likely to get disrupted or delayed due to non-issuance of drawings/ instructions.

v. All key staff employed at the site by the vendor shall be considered essential to the performance of the work and the Project Coordination Services, and all key staff shall be subject to the approval of the Owner’s Representative.  However such approval shall not relieve the vendor of any of its contractual obligations with respect to the staff employed by the vendor. No staff including the resident engineer and other technical supervisory staff shall be removed or transferred from the work without the prior written permission of the Owner’s Representative or IUCAA Estate Manager.

vi. The Owner’s Representative and IUCAA Estate Manager shall, however, have the authority to order the removal from Site of any undesirable personnel from vendor’s side due to their misconduct, incompetence or negligence in the performance of their duties. If key staff becomes unavailable for

performing the work or the Project Coordination Services for  reasons beyond the vendor’s control, the vendor shall immediately notify the Owner’s Representative to evaluate the impact of the same on the project. Prior to substitution or addition of any key staff, the vendor shall obtain the Owner’s Representative’s written consent as to the acceptability of replacement or additions to such personnel.

vii. The vendor shall at all times be solely responsible for the acts, omissions, defaults and neglect of all of its representatives, agents, servants, workmen and suppliers and those of its Sub-Contractors.

11.2 Man-power, plant and machinery:

i. The vendor shall at its own cost provide and install all equipment, materials, plant, cranes, hoists, ladders, and scaffolding, necessary for the execution of the work in conformity with the contract Documents to the satisfaction of the Owner’s Representative and IUCAA Estate Manager. All machines, tools, trucks, formwork material, man-power and everything else necessary for the proper and satisfactory execution and completion of the work in accordance with the Contract Documents shall be provided by the vendor at its own cost.

ii. The vendor shall within one week of the award of contract submit a complete list of its manpower, plant and machinery for the approval of the Owner’s Representative and IUCAA Estate Manager, which approval however, shall not relieve the vendor of any of its responsibilities, obligations and liabilities under the contract. The vendor shall augment its manpower, plant and machinery without extra cost to the Owner whenever required or so directed by the Owner’s Representative/IUCAA Estate Manager in order to conform to the approved construction programme for the achievement of milestones and Virtual Completion of the Work.

iii. All the tools, equipment and machinery provided by Contractor for the execution of the Project should be in perfect condition. Any fault or non-operation of the tools, equipment and machinery, shall be rectified immediately by the vendor and no time extension to the approved construction programme shall be allowed at all in the event of some fault of non-operation of tools, equipment and machinery.

11.3  Security: The vendor shall at its own cost provide at all times adequate number of watchmen/ security personnel to guard the Site, the materials and equipment, to the satisfaction of the Owner’s Representative/ IUCAA Estate Manager. The vendor shall at all times be fully responsible for the security of all materials and equipment on the site, whether it’s own or those of any sub-contractor. Neither the Owner nor the Owner’s representative / IUCAA Estate Manager shall be responsible for any loss due to theft, fire, accident or any other reasons, whatsoever. Additionally, the vendor shall, within seven days of the execution of the Contract, provide all necessary details of the security agency providing the watchmen/ security personnel for obtaining the written approval of the IUCAA Estate Manager.

11.4    Water and electricity: Tap off’s for temporary water and electricity shall be provided on site at single source ( free of cost ).  The vendor shall make its own arrangement thereafter from the Tap off’s for Works and all costs in relation thereto shall be borne solely by the vendor.

11.5   Scaffolding, Staging, Guard Rails, Barricades:  The vendor shall at its cost provide steel scaffolding, staging, guard rails, barricades and safety barriers around all openings and at all edges, temporary stairs and other temporary measures required during the project. The supports for the scaffolding, staging guard rails, barricades and safety barriers and temporary stairs shall be strong and adequate for the particular situations, tied together with horizontal pieces and braced properly. The temporary access to the various parts of the building under construction shall be rigid and strong enough to avoid any chance of mishaps. The entire scaffolding arrangement together with the staging, guard rails, barricades and safety barriers, and temporary stairs shall be to the approval of the IUCAA Estate Manager which approval shall not relieve the vendor of any of its responsibilities, obligations and liabilities in relation to the safety requirements and for timely completion of the Work in accordance with the approved construction schedule. The use of wooden scaffolding on the Site is strictly forbidden.

11.6 Safety Equipment: The vendor shall provide all the personal protective equipments like safety helmets, safety boots/shoes, protective clothing, etc., at its own cost to the Owner’s, Owner’s Representatives, IUCAA Estate Manager’s, Project consultant’s & their team within three days from the execution of the Letter of Intent of the Tender

11.7 Protection of Environment: The vendor understands that the Site must be free from pollutants at the time of access to the Site and commencement of the Work. The vendor shall comply with all applicable environmental laws and regulations and shall ensure that the site is and remains free from pollutants till the end of the project. The vendor shall ensure inter alia, that neither the soil nor the ground water is polluted or contaminated by fuels or lubricants emitted by machinery operated on the Site or by other dangerous or poisonous substances which are or are deemed to be hazardous to the environment. Notwithstanding the above, the vendor shall comply with all the directions and decisions of the IUCAA Estate Manager in this regard and all applicable environmental legislations in relation to the same including obtaining statutory consents and approvals as may be required.

Vendor  thereof.

The vendor shall ensure that all operations by the vendor, its workmen, employees, sub-contractors to complete the project and the remedying of any defects therein shall, so far as compliance with the requirements of this agreement permit, be carried on so as not to interfere unnecessarily or improperly with:

a) the convenience of the public, or

b) the Owner’s operation and utilization of the facility at the Site; and

c) the Work of Vendors. If any hazardous or obnoxious materials (as defined by Indian law) are specified for use or are being used by vendors, the vendor  shall keep record of such material and forthwith give written notice to the Owner and shall ensure that the sub-contractors and Vendors, as applicable, use, store and dispose of such hazardous or obnoxious materials strictly in accordance with all applicable laws.

12.0 Additional Safety Regulations: The vendor shall continuously maintain adequate protection for the work against fire and other hazards and shall protect the Owner’s property and the site from damage or loss during the performance of this contract. The vendor also shall adequately protect property adjacent to the Site.

The vendor shall take all necessary precautions for the safety of its employees, sub-contractors and the vendors performing the work and shall comply with all applicable safety laws and regulations to prevent accidents or injury to persons on, about, or adjacent to the site. The vendor shall be responsible for co-ordinating a safe working  programme with the Owner’s Representative and the IUCAA Estate Manager. Such a programme shall include, and the vendor shall be responsible for maintaining, the following safe working conditions and practices:

i. All combustible material, food matter, garbage, scrap, and other debris generated during the performance of the work shall be collected and removed from the site daily. Arrangements for scrap burning should be discussed with Owner’s representative.

ii. An adequate number and type of fire extinguishers shall be provided at the site for fire control and shall be kept/maintained in satisfactory and effective working condition, at all times.

12.1 Requirement of Fire Extinguishers  Each gas welding or burning, arc welding unit, tar pot, or open flame unit requires a fire extinguisher with it during operation.

12.2 Requirement of Equipment : The availability of fire blankets is recommended at the site. Other equipment related conditions are as follows:

i.   The vendor shall use all equipment, which is in good condition. The vendor shall not use or permit to be used the Owner's equipment and the Owner shall not use the vendor's equipment without prior written permission of the other.

ii.  When working in an occupied building or area, the vendor must before commencement of work familiarise itself with the hazards of that area, such as the location of flammable substances and toxic fumes.

iii.  Materials and equipment intended for installation in the work as well as the Owner's equipment and materials already in place are to be protected at all times from debris, weather, or any damage. The vendor shall take all steps necessary to ensure the preservation condition of such equipment.

iv.  The vendor's materials, tools, and equipment shall be stored only in areas approved by the Owner for this purpose.

v. Site access and parking by the vendor's personnel shall be at locations designated by the Owner/ IUCAA Estate Manager.  Only the vendor's personnel necessary for the performance of the work shall be permitted access to the site. The vendor and its employees and sub-contractors shall adhere to all speed limits and traffic regulations at the Site.

vi. The vendor and its employees and sub-contractors shall strictly obey all "No Smoking" restrictions.

vii. The vendor shall not operate or use or manipulate utilities at the site without the Owner's prior written approval.

viii. No valves shall be turned off or on, or electrical disconnect switches operated except in an emergency. Any required utility "shut downs" will be scheduled and co-ordinated by the Owner’s representative.

ix. The vendor shall make any requests for utility manipulation or "shut downs" in writing to the IUCAA Estate Manager at least five days advance notice.

12.3. Safety with regard to site and housekeeping:

i. The use of intoxicants or unlawful drugs at the site, in any degree, shall be strictly prohibited. The vendor shall rigorously enforce this regulation.

ii. When overhead work is in progress in or around an occupied area, signs to denote such work prominently displaying “Overhead Work” shall be used or the area shall be protected by barricade.

iii. Dusty work, such as concrete breaking or demolition, in or near occupied areas, shall proceed only after wetting down the area and taking steps necessary to prevent dust from penetrating occupied areas and creating a nuisance.

iv. Care shall be taken not to block any door, passageway, safety exit, firefighting equipment, or safety equipment with materials or equipment.

v.  Vendor shall maintain general cleanliness at site. All waste and debris shall be stored at designated place and disposed regularly.  Site should be cleaned as per instruction given by Estate Manager at the end of day.

vi.  Materials must be piled, stacked, or stored in a neat and orderly manner.  All stacking, whether inside or outside a building, shall be parallel to or at right angles to the building line or fence.

vii.  When noisy operations of a prolonged nature are necessary in or near an occupied area, arrangements must be made with the Owner’s Representative for scheduling to minimize any nuisance in the occupied area.

12.4 Non-compliance of Regulations : If the IUCAA Estate Manager or the Owner’s Representative notifies the vendor of non-compliance with the foregoing regulations, the vendor shall immediately, if so directed, or in any event not more than Twenty four (24) hours after receipt of such notice, make all reasonable efforts to correct/ rectify such non-compliance.  If the vendor fails to do so, the Owner may suspend all or any part of the work. The, Owner shall lift the suspension of the work only upon the satisfactory corrective action undertaken by the vendor in this regard. The vendor shall not claim any extension of time to complete the work or additional fees due to any such work suspension.

12.5 Implementation of Safety Measures Notwithstanding anything herein before contained, particularly in clause 12.3,

12.6  The vendor shall be liable to ensure and implement all safety measures, whether or not statutorily prescribed, to safeguard, preserve and protect the life, health and welfare of every workman employed/deployed/engaged directly or indirectly by the vendor on the site and in relation to or connected with the Work and all vendors employed in later phases of the project in addition to installing, providing every prescribed safety and protective equipment, clothing etc., and the mere absence of any reference to or specification of a particular statute or rule or regulation in this contract shall not absolve the vendor of an obligation to comply with every such law, rule or regulation. The vendor shall be liable for all consequences/liabilities arising out of its violating any of the aforesaid provisions, including fines, penalties, compensations, damages, prosecutions, proceedings, medical expenditure and costs, rehabilitation costs and all other expenses connected therewith.

13 CONTRIBUTION TOWARDS EMPLOYEE BENEFITS, FUNDS ETC.: The vendor shall include in the contract price all expenses necessary to  meet its obligations for making contributions toward employee benefits funds (such as provident fund, ESI benefits, old age pension and/or any other benefits/compensation legally payable) in compliance with all the statutory regulations and requirements. All records in this connection shall be properly maintained by the vendor and produced for scrutiny by the concerned authorities, IUCAA Estate Manager and the Owner whenever called for.

14 SETTING OUT AND SITE SURVEYS: The vendor shall establish, maintain and assume responsibility for all bench marks and grid lines, and all other levels, lines, dimensions and grades that are necessary for the execution of the work, in conformity with the Contract Documents. The vendor shall establish its relation to the permanent benchmarks and boundary lines established at the site. The vendor shall verify and co-relate all the survey data available at the Site before commencing the work and shall immediately report in writing any errors or inconsistencies to the IUCAA Estate Manager. Commencement of Work by the vendor shall be regarded as its acceptance of the correctness of all survey and setting out data available at the Site and no claims shall be entertained or allowed in respect of any errors or discrepancies found at a later date. If at any time error in this regard appears during its progress of the work, the vendor shall at its own expense rectify such error to the satisfaction of the IUCAA Estate Manager/ Owner. The approval by the IUCAA Estate Manager of the setting out by the vendor shall not relieve the vendor  of any of the responsibilities, obligations, and liabilities under the contract.

The vendor shall be entirely and exclusively responsible for the horizontal, vertical and other alignment for all levels and dimensions and for the correctness of every part of the work, and he shall rectify effectively any errors or imperfections therein. All such rectifications shall be carried out by the vendor at its own cost and to the instructions and satisfaction of the IUCAA Estate Manager. The vendor shall employ qualified surveyors to carry out all the surveys and setting out works in this regard.

15 DRAWINGS, SPECIFICATIONS, INTERPRETATIONS ETC.:  Within 10 days from the issue of Letter of Intent/ Purchase/Work Order, the vendor shall be furnished by the IUCAA Estate Manager and/or Owner’s Representative with one copy each of the conditions of contract, specifications, and schedule of rates, without cost to vendor for its own use and for the use of its sub-contractors until the completion of the contract. Additional copies of contract documents will be supplied on payment at actual cost basis. Three copies of the working drawings shall be provided by the project consultant through IUCAA Estate Manager to the vendor as the work progresses. The time and the date for the provision of the drawings shall be mutually agreed between the vendor and Owner’s representative / IUCAA Estate Manager / Project consultant in conformity with the construction programme and with due regard for the need to order and specify materials and equipment to the site. In general, the drawings shall indicate the dimensions, positions and type of construction, the specifications shall stipulate the quality and the methods and performance criteria, and the schedule of rates shall indicate the rates for each item of work for evaluating change orders.  However, the above contract documents being complementary, what is called for by any one shall be binding as if called for by all.  Matters not contained in the specifications and in case of any ambiguities in the written specifications of the contract, the works shall be executed as per relevant BIS codes and CPWD specifications in that order of preference.  If such codes have not been framed, the decision of the project consultant in the matter shall be final and binding on the vendor. Any work indicated in the drawings and not mentioned in the specifications or vice versa, shall be deemed as though fully set forth in the drawings or specifications as the case may be.  Work not specifically detailed, called for, marked or specified, shall be the same as similar parts that are detailed, marked or specified. From time to time during the progress of the work, the vendor will be issued with revisions of drawings and written instructions by the IUCAA Estate Manager in connection with and necessary for the proper execution and successful completion of the work.   All such revisions of drawings and written instructions shall be part of the contract documents and the vendor shall be bound to carry out the work that is shown and detailed on all such drawings and shall be bound to follow and comply with all such  instructions. All drawings and their subsequent revisions will be issued to the vendor by listing such drawings on the transmittals by the Project Manager. The vendor shall maintain a drawing register listing all drawings and their latest revisions. All superseded drawings shall be so stamped and withdrawn from circulation at the site. It shall be the responsibility of the vendor to ascertain and ensure that all the work is carried out in accordance with the latest revisions of the drawings issued to him.  if the Contractor fail to do so, all the rectifications and remedial work that may be required to conform to the latest revisions of the drawings shall be at the vendor's sole expenses.

Wherever it is mentioned in the conditions of contract, specifications, and other contract documents that the vendor shall perform certain work or provide certain facilities, it is understood that the vendor shall do so at its own cost, unless otherwise provided in the said documents.

The vendor shall immediately in writing bring any errors or inconsistencies in the drawings and specifications to the attention of the IUCAA Estate Manager for interpretation or correction before proceeding with the affected portion of the work, and no claims or losses alleged to have been caused by such discrepancies shall be entertained or allowed at any stage. Local conditions, which may affect the work, shall likewise be brought to IUCAA Estate Manager attention at once.  If at any time it is discovered that work, which has been done or is being done is not in accordance with the approved drawings and specifications, the vendor shall correct the work immediately. Correction of such work shall be at the expense of the vendor and shall not form a basis for any claims for payment or extension of time. The vendor shall carry out all the rectification work only after obtaining the approval for the same from IUCAA.

The vendor, in the execution of the work, shall make no deviations from the drawings, specifications, and other contract documents. Interpretations and clarifications shall be issued by the Project Consultant / IUCAA, which shall be binding on the vendor.

No scaling of any drawing shall be done to obtain the dimensions. Figured dimensions on the drawings shall be used for carrying out the work. Drawings with large-scale details shall take precedence over small scale drawings. Where any drawings and details have not been provided but are necessary for the execution of the work, it shall be the responsibility of the vendor to seek these drawings and details in writing from IUCAA Estate Manager at least four weeks prior to the latest date by which the vendor needs these drawings and details to suit the programmed execution of the work. No extension of time shall be allowed for any delays caused due to the vendor's failure to seek such details.

Drawings, schedule of rates, specifications, and other contract documents, and all copies thereof furnished by the project manager shall be treated the Owner's property at all times.  Such drawings, schedule of rates, specifications, and other contract documents shall not be used on any other work and shall be returned to the Owner at its request or at the completion of the work in accordance with the contract. In case of any discrepancy in the interpretation of drawings, the decision of IUCAA shall be binding.

16. ASSIGNMENT AND SUBLETTING : The vendor shall not assign this contract or any part of it. The vendor may, however, sub-contract any part of the work with the prior written consent of IUCAA. The Owner/ Owner’s representative/ Project consultant/ Estate Manager  reserves the right to review and approve each sub-contractor which the vendor  recommends at any time to engage to perform any services before such sub-contractor is hired or performs any service. Any permission to sub-contract any parts of the work shall not relieve the vendor from any of its responsibilities, obligations, and liabilities under this contract.

17. NOMINATED SUB-CONTRACTORS: As soon as practicable, but at least one week before awarding any sub-contract, the vendor shall submit to the project consultant, IUCAA Estate Manager and the Owner’s representative in writing the names of the nominated sub-contractors proposed for any part of the work, for the approval of the same by the project consultant / IUCAA . The vendor shall employ such sub-contractors only after he has received confirmation in writing of such approval from Estate Manager and the Owner’s representative. Such approval, however, shall not relieve the vendor of any of its responsibilities, obligations and liabilities under the contract. The contractor shall be responsible for the acts, defaults, omissions and neglect of all sub-contractors and their agents, servants and workmen. The vendor shall not employ any sub-contractor to whom Estate Manager or the Owner’s representative object and/or does not approve. The project consultant may by written instruction inform the vendor, waiving the need for the project consultant to specifically approve the sub-contractors in addition to the approval of IUCAA.

18.SEPARATE CONTRACTS: The Owner reserves the right to enter into separate other contracts in connection with the project. The vendor shall afford other contractors reasonable opportunity for their access to the site, for the storage of their materials, and for the execution of their work, or if specified give assistance to such vendors for such purposes as are specified. The vendor shall properly connect and co-ordinate its work with that of the other contractors that may be employed or engaged by the Owner. If any part of the contractors's work depends for its proper execution or results upon the work of any other contractors, the vendor shall inspect and promptly report in writing to IUCAA, any defects in such work that render it unsuitable for such proper execution and results.  The vendor's failure to inspect and report such defects shall constitute as an acceptance of the other contractor's work as fit and proper for receiving the work of the vendor.

19.CO-ORDINATION OF WORK : At the commencement of the work, and from time to time, the vendor shall cooperate with other contractors, sub-contractors, persons engaged on separate contracts in connection with the project, vendors and the project consultant and with the Owner’s representative for the purpose of the co-ordination and execution of various phases of the project. The vendor shall determine and ascertain from the contractors and persons engaged on separate contracts, in connection with the project, the extent of all chasings, cutting and forming of all openings, holes, details of all inserts, sleeves, etc. that are required to accommodate the various services.

The vendor shall determine and ascertain the routes of all services and positions of all floor and wall openings, outlets, traps, the details of all inserts, equipment and services and shall carry out the construction and making good of all "builder's work" in accordance with and as shown, described and/or measured in the drawings, specifications, and other contract documents. Also, the vendor shall ensure that all required services, inserts, sleeves, embedment etc. are in place/position before he proceeds with its work.  If the vendor fail to comply with these requirements and the consequence of such failure necessitates the breaking, re-doing and making good of any work, then the cost of all such breaking, re-doing and making good of any work shall be to the account of the vendor and shall be borne by him. No breaking and cutting of completed work shall be done unless specifically authorised in writing by IUCAA Estate Manager.  No work shall be done over broken or patched work without first ascertaining that the broken surface is adequately prepared and reinforced to receive and hold further work, as determined by Estate Manager. In order to ensure proper co-ordination is being undertaken, weekly meetings, chaired by SAO / IUCAA authorities will be held with the various contractors and at which coordination will be discussed and minutes of actions proposed circulated.

20. WORK ON NON WORKING DAYS:   If it is necessary for the vendor or any sub-contractor to work on days other than working days or outside the normal working hours in order to keep up to the time schedule and meet the construction programme, the vendor shall obtain the prior approval of IUCAA in writing. Even if any work is carried out at site on a non working day with prior written permission of IUCAA, the vendor shall be solely responsible for extra cost including but not limited to wages. Applicability of all other terms and conditions of contract on such days would be same as applicable for a Working day.

21. MATERIALS, WORKMANSHIP, STORAGE, INSPECTIONS ETC.:

21.1 Materials and workmanship: The vendor shall be responsible for the establishment of a full and comprehensive quality control system for the work. The system shall include, but not be limited to, the means of controlling the testing and receipt of materials, the inspection of the work, the filing and ordering of drawings and correspondence and the duties and responsibilities of staff members.

All materials and equipment to be incorporated in the work shall be new and original. The materials, equipment, and workmanship shall be of the best quality of the specified type, in conformity with contract documents and the best engineering and construction practices, comply with the specifications and to the entire satisfaction of IUCAA. This requirement shall be strictly enforced at all times and stages of the work and no request for change whatsoever shall be entertained on the grounds of anything to the contrary being the prevailing practice. The vendor shall immediately remove from the work any materials, equipment and/or workmanship which, in the opinion of IUCAA Estate Manager  are defective or unsuitable or not in conformity with the contract documents and best engineering and construction practices, and the vendor shall replace such rejected materials, equipment and/or workmanship with proper, specified, and required and approved materials, equipment and/or workmanship, all at its own cost within a period of seven (7) days from the date of  issuance of such notice.

The vendor shall, whenever required to do so by IUCAA Estate Manager   immediately submit satisfactory evidence and necessary test results as to the kind and quality of the materials and equipment.

21.2 Special makes or brands:  Where special makes or brands are called for, they shall be mentioned as a standard brand or make. Others brands or special makes of equivalent quality may be used provided the substituted materials are equivalent to the brand specified, and prior approval for the use of such substituted materials is obtained in writing from IUCAA Estate Manager. Unless substitutions are approved by the IUCAA in writing in advance, no deviations from the specifications and other contract documents shall be permitted. The vendor shall indicate and submit written evidence of the substituted material or equipment called for in the specifications and other contract documents that are not obtainable for incorporation in the work within the time limit of the contract. Failure to indicate this in writing within two weeks of the signing of the contract will be deemed as sufficient cause for denial of any request for an extension of time because of the same. Alternative equivalent brands if suggested by the vendor during construction may be considered provided the suggested brand fully meets the requirements and is acceptable to IUCAA. Any variation in price due to the use of alternate brands shall be permissible provided it is pre-approved in writing by the Owner’s representatives.

21.3 Proper scheduling and delivery of materials: All materials and equipment shall be scheduled and delivered so as to ensure a speedy and uninterrupted progress of the work, and the same shall be properly stored.

21.4 List of Materials: Within seven (7) days of the signing of the contract, the vendor shall submit for the approval of the IUCAA a complete list of all materials and equipment the vendor and its sub-contractors propose to use in the work, of definite brands or makes, which differ in any respect from those specified, or the particular brand where more than one is specified as standard. The vendor shall also list items not specifically mentioned in the contract documents but which are reasonably inferred and are necessary for the proper execution and successful completion of the Work.

21.5 Right Type of Workmen, Plant And Machinery, Jigs, Tools, Etc.:  The vendor shall employ the right type of workmen, plant and machinery, jigs, tools etc. to fabricate and/or install all materials and equipment. Such material and equipment shall be fabricated and/or installed without any damage and in accordance with the material/ equipment manufacturer's instructions and manuals, and to the satisfaction of IUCAA Estate Manager.

21.6 Inspection:  All materials, equipment, and workmanship shall be subject to inspection, examination and testing at all times and stages during construction, manufacture and/or installation, by IUCAA Estate Manager and they shall have the right to reject and order the removal and replacement of any defective material, equipment and / or workmanship or require its correction and rectification. The contractor shall not proceed with any operation or sequence or trade of the work until the previous operation or sequence or trade has been inspected and approved by IUCAA. No embedded items or any other work shall be covered up unless these have been inspected and approved by IUCAA Estate Manager. The onus shall be on the vendor to get such inspections carried out and obtain such approvals.  If the vendor fail to comply with these requirements, then all additional or redoing of work necessitated as a consequence thereof shall be at the vendor's cost and expense. No inspection or approval shall relieve the vendor of any of its responsibilities, obligations and liabilities under the contract. No defective workmanship shall be repaired or patched up in any way without inspection and direction of IUCAA Estate Manager. Rejected workmanship shall be immediately corrected and rectified and rejected materials and equipment shall be removed and replaced with proper, specified and required materials and equipment, by the vendor to the approval and satisfaction of IUCAA. The cost of all such correction and rectification and such removal and replacement shall be to the account of the vendor and shall be borne by him, and also, they shall be responsible for all delays in this regard. The vendor shall promptly segregate and remove the rejected materials and equipment from the site and shall not reuse them in the work. If the vendor fails to proceed at once with the correction and rectification of rejected workmanship and/or the removal and replacement of rejected materials and equipment, the Owner shall have the right to employ other persons / agencies to correct and rectify such workmanship and/or remove and replace such materials and equipment, and recover the cost there of from the vendor, or the Owner may terminate the right of the vendor to proceed further with the work.

The vendor shall furnish promptly and without any charge, all facilities, access, labour, materials, plant and tools required and necessary for enabling IUCAA Estate Manager, to carry out inspections and tests in a safe and convenient manner. The vendor shall ascertain and ensure that the facilities and access provided for the carrying out of all inspections are completely safe in every respect and the vendor shall be fully responsible and liable for all matters in connection with such safety.

21.7 Testing:  All the tests on materials, equipment, and workmanship that shall be necessary in connection with the execution of the work, as decided by IUCAA and as called for in the contract documents, shall be carried out at the cost of the vendor at the place of work or of manufacture or fabrication or at the site or at an approved testing laboratory or at all or any such places. The vendor shall provide all transportation, assistance, instruments, machines, labour and materials as are required for the examining, measuring and testing as described above, and all expenses connected with the tests as described above shall be borne by the vendor.

21.8 Certificates:  The vendor shall furnish, at its own cost, test certificates for the various materials and equipment as called for. Such test certificates shall be from the manufacturer for the particular consignment/lot/piece and shall be duly authenticated by respective consultants. The details in respect of the test certificates shall be as decided by IUCAA (in consultation with consultants) for the relevant items.

21.9 As built drawings : The vendor shall during the course of execution, prepare and keep updated a complete set of " as-on-date as built drawings” reflecting current status of construction, marked with each and every change from the contract drawings. Three sets of "as built" drawings as agreed shall be supplied to IUCAA Estate Manager  upon completion of project, along with a soft copy of the drawings in AutoCAD format (specified version) at no extra cost to the owner.

21.10 Daily site reports:  The vendor shall throughout the contract period, submit daily site reports to the project manager and the Owner’s representative. The reports will include, but not be limited to:

i. Record of the site progress

ii.Number of employees, workmen. labour engaged on the Site

iii.Number of men employed on individual trades

iv. Plant and machinery at site (including an indication as to whether the plant is working or standing)

v. Notification of accidents

vi. Material received at site on that specific day

vii. Events influencing the progress of the Work

22 BUREAU OF INDIAN  STANDARDS:  (BIS )  Indian Standards Specifications a reference made to any Indian Standards Specifications in the contract documents shall imply reference to the latest version of that standard, including such revisions / amendments as may be issued, during the currency of the contract, by the Bureau of Indian Standards (BIS) and the corresponding clause/s therein shall hold valid in place of those referred to. The vendor shall keep copies at the site of all latest publications of relevant Indian Standard Specifications applicable to the work at the site, as listed in the specifications.

22.1. Amendments to BIS:  If any Amendments to BIS codes is announced after finalization of the contract the same shall be deemed to be incorporated into the specifications, wherever applicable.

22.2. Tolerances:  In case the work does not conform to the dimensions and limits of tolerances specified in the contract documents and/or the Indian Standard Specifications the vendor shall be liable for all costs and expenses incurred for rectifications and/or replacements of any other contractor's and/or Sub-contractor's work required, in accordance with the directions of the Estate Manager, for the proper installation of the finishing elements and/or equipment, and/or for structural purposes. The Estate Manager’s decision in this respect shall be final and binding on the contractor and sub-contractors, and all such costs and expenses shall be recovered from the pertinent contractors and sub-contractors and shall be deducted by the Owner from any money that may be payable or that may become payable under the contract to such pertinent contractors and sub-contractors for and on behalf of the vendor.

23. PROTECTION OF WORKS: The vendor shall take full responsibility for the proper care and protection of the work carried out in respect of the project from commencement until completion and handing over of the project to IUCAA. The vendor shall protect and preserve the work carried out in respect of the Project in every way from any damage, fire or accident, including by providing temporary roofs, boxing or other construction as required by IUCAA. This protection shall be provided for all property on the site as well as adjacent to the Site. The vendor shall adequately protect, to the satisfaction of the Estate Manager, all the items of finishing work to prevent any chipping, cracking, breaking of edges or any damage of any kind whatsoever and to prevent such work from getting marked or stained or dirty. If  the vendor fail to protect the work in respect of the project or any part thereof and should any damage be caused to the same, the vendor shall be responsible for all replacement and rectification, as directed by the Estate Manager, and all costs and expenses in connection with such replacement and rectification shall be to the account of the vendor and shall be borne by it. The vendor shall in connection with the work provide and maintain at its own cost all lights, security guards, fencing and anything else necessary for the protection of the work and for the safety of the public and everyone associated with the work, all to the approval and satisfaction of the Estate Manager. All operations necessary for the execution of the work shall be carried out so as not to interfere with the convenience of the public, or with the traffic, or the access to, use and occupation of public or private roads and footpaths or of properties whether in the possession of the Owner or of any other person. The vendor shall hold the Owner harmless and indemnify the Owner in respect of all claims, proceedings, damages, costs, charges, and expenses whatsoever arising out of or in relation to any such matters.

24. CLEANING OF WORKS AND CLEARING OF SITE: The vendor shall maintain the site and all work thereon in neat, clean and tidy-conditions at all times. The following shall be ensured by the vendor in the regard:

i. The vendor shall remove all rubbish and debris from the Site on daily basis and as directed by the Estate Manager. Suitable steel skips shall be provided at strategic locations around the site to receive waste and packaging materials.

ii. Just prior to the virtual completion of the work, or whenever so directed by the Estate  Manager, the vendor shall carry out all the work necessary to ensure that the site is clear and the work are clean in every respect, the surplus materials, debris, sheds and all other temporary structures are removed from the site, all plant and machinery of the vendor are removed from site, the areas under floors are cleared of rubbish, the gutters and drains are cleared, the doors and sashes are eased, the locks and fastenings are oiled, all electrical, plumbing and other services are tested and commissioned, the keys are clearly labeled and handed to the Estate Manager, so that at the time of virtual completion the whole Site and the work are left fit for immediate occupation and use, to the approval and satisfaction of the Estate Manager, and the Owner’s representative.

iii. If the vendor fail to comply with the cleaning requirements, whether progressively or before completion, or fail to clear the site as directed and required, then the Estate Manager, after giving due notice in writing to the vendor, shall have the right to employ other persons or agencies to carry out the cleaning and/or clearing work and all costs incurred on such work shall be recovered from the vendors

and shall be deducted by the Owner from any money that may be payable or that may become payable to the vendor.

25. METHOD OF MEASUREMENT:  To evaluate any additional work instructed under change orders by the Estate Manager or the Owner’s representative, the standard method of measurement shall be in accordance with the standards laid down by Bureau of Indian Standards (IS:1200) shall be followed. However if definite methods of measurements are stipulated in the schedule of rates or specifications, then the same shall supersede BIS methods and shall be followed. In the event of any dispute with regard to the method of measurement of any work, the decision of the Estate Manager shall be final and binding and no extra claims shall be entertained or allowed at any stage in this regard.

26.COVERING UP : The vendor shall give at least 24 hours clear notice in writing to the Estate Manager before covering up any of the work in foundations or any other such areas in order that inspection of the work may be carried out for maintaining proper quality control. In the event of the vendor failing to provide such notice he shall, at its own expense, uncover such work as required to allow the inspection to be taken and thereafter shall reinstate the work to the satisfaction of the Estate Manager.

27 PAYMENTS AND SECURED ADVANCE:

- No advance will be paid before commencing the work.

- IUCAA may pay only 50% secured advance against approved material brought at site by vendor.

- Only three RA bills will be allowed to be raised before final billing, which should not be less than Five Lakhs each.

- On submission of final bill 75% of assessed bill value shall be paid on ad hoc basis and balance will be released after verification from accounts.

27.1 Running Bills :  The vendor shall prepare measured bills as directed by the Estate Manager (detailed measurement, abstract sheet, deviation statement for ongoing and completed work, materials reconciliation statement and any specific instructions which may be given in this regard by the Estate Manager and other supporting documents incase if it is required) .

27.2 Payment Certificate: The Estate Manager shall issue a payment certificate within the number of working days as reflected in tender documents, from the date of the bill received from the vendor for the value of work (net amount due to the vendor after deductions) executed by the vendor, provided all supporting detailed measurements, abstract sheets and other supporting documents requested by the Estate Manager are furnished at the time of submission of such bills. Thereafter, the vendor shall be paid by the Owner of certified amount (after deduction of applicable retention, TDS and WCT), within 15 days as per IUCAA standard terms.

27.3 Retention Money & Final Bill:  The Retention Money will be held @ 5% of the final bill value. Security deposit will be converted to retention amount and it will be released only after completion of defect liability period of three years from the date of completion of project.

Final Bill will be released only after completion of the project and duly certified by the Project consultant/ Estate Manager.  Payment of final bill will be made within one month subject to submission of complete documents.

27.4 Withholding of payments:  The Estate Manager may withhold payment on account of subsequently discovered evidence, and nullify the whole or a part of any payment certificate to such extent as may be necessary to protect the Owner from loss on account of including but not limited to the following:

i.      Defective work not remedied by the vendor, non compliance notices not attended by the

vendor.

ii.      Failure of the vendor to make payments properly and regularly to its own workers, to its sub-

contractors, to its suppliers.

iii.     Damage by the vendor to the work of other contractors, sub-contractors or vendors.

iv.     A reasonable doubt that the contract cannot be completed for the balance unpaid amount.

v.      A reasonable doubt that the vendor intends to leave work items incomplete.

vi.     Failure of the vendor to execute the work in conformity with the contract documents.

vii.    Failure of the vendor to meet or keep-up with the approved SITC programme on which

the agreed payment schedule is based.

viii.   Failure of the vendor to comply with and fulfill all contractual obligations and liabilities

stipulated in the contract documents.

ix.    Failure of the vendor to submit proofs of payment of necessary ESI, PF payments for his workers.

28 RECTIFICATION OF IMPROPER WORK NOTICED: If it shall appear to the Estate Manager or the Owner’s Representative during the progress of the work that any work has been executed with unsound, imperfect or unskillful workmanship or with materials of any inferior description or that any materials or articles provided by the vendor for the execution of the work are unsound or of a quality inferior to that contracted for or otherwise not in accordance with the contract, the vendor shall, on demand in writing from the Estate Manager, specifying the work, materials or articles complained of, notwithstanding that the same may have been passed and certified by the Estate Manager, forthwith rectify or remove and reconstruct the work so specified in whole, or in part as the case may require or , remove the materials or articles so specified and provide other proper and suitable materials or articles at its own proper charge and cost and in the event of its failing to do so within a period so specified by the Estate Manager in its demand aforesaid, the Estate Manager may rectify or remove and re-execute the work or remove and replace the materials or articles complained of as the case may be by engaging a third party contractor at the risk and expense in all respects of the vendor, and deduct the expenses from the retention money or any sums that may be due at any time thereafter may become due to the vendor or from the performance bond executed by the vendor.

29 CHANGE ORDERS:

29.1 Change in scope of work: The Owner reserves the right to alter the scope of work as per tender documents  and consequently the contract price shall be suitably adjusted for such changes by reference to the rates in the schedule of rates. The Estate Manager shall issue all change orders only after obtaining the prior written consent of the Owner’s representative. The vendor shall not proceed with additional scope of work without prior approval from Owner/ Owner’s representative through project consultant.

29.2 Rates for additional, altered or substituted work if the rates for the additional, altered or substituted work are not specifically provided in the schedule of rates then such rates shall be derived from the rates that are specified for a similar class of work in the contract. The Estate Manager’s interpretation in consonance with the Owner as to what is a similar class of work and its decision on the method in which the rate is to be derived shall be final and binding on the vendor. If the rates for the additional, altered or substituted work cannot be determined in the manner specified above, then the rates for such work shall be determined on the basis of actual consumption of materials, and actual use of labour and plant and machinery, as detailed below:

i.   Cost of materials supplied by the vendor, at not more than prevailing market rates, actually

incorporated in the work.

ii.  Cost of labour actually used at the site on the work at prevailing rates of  labour.

iii. Cost allocation toward the work for the use of any plant and machinery at the site, on actual basis.

iv. 15% of the actual costs in respect of (i), (ii), and (iii) above, towards vendor's establishment and all

other costs and overhead and profit plus taxes as applicable shall be reimbursed. Vendor's

overheads and profit shall not be allowed on free issue items.

29.3 Approval from Owner/Owner’s representative:  Before the vendor undertakes any extra work, he shall ensure that he has received a specific change order, signed by the Estate Manager. No additional payments shall be made to the vendor without prior agreement and receipt of the necessary signed change order.  Each change order shall clearly state the value of the additional work agreed to and signed for by the Owner. The vendor shall at weekly  intervals submit to the Estate Manager an account giving particulars, as full and detailed as possible, of additional work ordered in writing by the Owner and which the vendor has executed during the preceding month. If any change order instructed by the Estate Manager causes a delay in the completion of the work causing the vendor to overrun the time fixed for completion of the work, the Owner shall agree, following joint review of the circumstances with the Estate Manager as to the extent of the delay, to postpone the time for completion of the Work by the period of delay, provided the vendor has notified the Owner in writing, of such expected delay before such change order is actually issued by the Estate Manager..

30 DEDUCTIONS FOR UNCORRECTED WORK: If the Estate Manager deems it inexpedient to get corrected or rectified any work of the vendor which is defective or damaged or of substandard quality or is generally not in accordance with the contract documents, then an equitable and appropriate deduction shall be made thereof from the contract price, and the project consultant’s and Estate Manager’s decision in this respect shall be final and binding on the vendor.   Furthermore if, by reason of any accident, or failure, or other event occurring to, in or in connection with the work, or any part thereof, either during the execution of the work or during the Defects Liability period, any remedial or other work or repair shall, in the opinion of the Estate Manager, be urgently necessary for the safety of the work, or any part thereof, and the vendor is unable or unwilling to immediately do such work or repair, the Owner may employ and pay other persons or agencies to carry out such work or repairs as the Estate Manager may consider necessary. If the work or repair so done by the other persons or agencies is work which, in the opinion of the Estate Manager, the vendor was liable to do at its own expense under the contract, then all expenses incurred by the Owner in connection with such work or repair shall be recovered from the vendor and shall be deducted by the Owner from any money that may be payable or that may become payable to the vendor or from the vendor’s performance bond, executed by the vendor in favour of the Owner.

31 TIME FOR COMPLETION:

31.1 Time-essence of contract: The time allowed for carrying out the work as entered in the tender shall be strictly observed by the vendor and shall be deemed to be of the essence of the contract and shall be reckoned from the date of award of the contract. The work shall proceed with due diligence until final completion. The vendor shall prepare a SITC  programme with time schedule keeping in view the completion period stipulated for specific portions of the work and also the overall completion time and submit the same for the approval of the Estate Manager and the project consultant. The vendor shall comply with the time schedule as approved by the Estate Manager and the Project Consultant. In the event of the vendor failing to comply with the overall and individual milestones contained in the time schedules, he shall be liable to pay liquidated damages as provided for in this contract.

31.2 Causes of delay for which claims for extension of time may be considered; The vendor may request claim for extension of time, subject to the conditions stated herein, should he be delayed or impeded in the execution of the work by reason of the following (decision of IUCAA authorities in this regards will be binding on the contractor):

i. Force Majeure;

ii. Any approved changes in the scope of work directed by Owner, project consultant, which in the opinion of the Estate Manager entail the requirement of additional time for completion of the Work.

31.3 Extension of Time : If the vendor suffers delay or incurs expense from failure on the part of the employer to give possession in accordance with the terms of this clause the engineer shall grant an extension of time for the completion of the works and certify such sum as in his sole opinion, shall be fair & final to cover the expense incurred which sum shall be paid by the employer.

31.4 Permission for Extension of Time: Request for an extension of time if any, for completion of the work by the vendor on the grounds of his having been unavoidably hindered in its execution, or any other grounds, shall be made in writing to the Engineer-in-Charge within 30 days of the date of the hindrance, on account of which he desires such extension as aforesaid, and the Engineer-in-Charge shall, if in his opinion (which shall be final) find that reasonable grounds have been shown, may authorize such extension of time as may in his opinion be necessary or proper.

31.5 Deletions or changes in the scope of the Work :  Should any deletions or changes in the scope of the work reduce the time required to complete the work under the contract, then the time savings accruing from such deletions may be considered by the Estate Manager in offsetting the durations awarded for an extension of time.

32. NO FINANCIAL OR OTHER COMPENSATION FOR DELAYS BY CONTRACTOR: The vendor shall not be entitled to any compensation for any loss suffered by him on account of delays in commencing or in executing or in completing the work, whatever might be the cause of the delay if such delay is on account of the vendor.

33. PROPRIETY OF EXECUTED WORK:  All executed work, whether in part or in whole shall be the exclusive property of the Owner. The Estate Manager, the Owner, the vendor or any of its sub-contractors or their employees or workmen or servants or agents shall not be entitled to the use of any such work except for the purpose of carrying out subsequent work that is required to be carried out under the contract or to complete the project. The Owner shall have the right to occupy and take over the work or any part thereof at any time during the progress of the work or upon their completion, irrespective of any pending claims or disputes that the vendor may have against the Owner.

34. INDEMNITY:

34.1 Indemnity by Vendor:   The vendor shall indemnify, defend and hold and keep indemnified, the Owner from and against all actions, suits, claims costs, liabilities and demands brought or made against the Owner in respect of any matter or thing done or omitted to be done by the vendor or any of its sub-contractor(s) or their employees, workmen, representatives, agents, servants or suppliers in the execution of or in connection with the work or the vendor's or sub-contractor's performance under this contract and against any loss or damage to the Owner in consequence of any action or suit being brought against the vendor or any of its sub-contractor(s) or their employees, workmen, representatives, agents, servants or suppliers for anything done or omitted to be done in execution of the work and the project coordination services under this contract, including but not limited to meeting the project milestones, noncompliance with the applicable laws and regulations of the government and local authorities, not obtaining the relevant licences and permits, infringing any patents rights and specifically regarding use, storage and disposal of hazardous materials. The obligations of the vendor under this clause shall survive till the closure of Defects Liability period.

34.2 Indemnity by Sub-Contractors:  The vendor shall ensure that the sub-contractors indemnify, defend and hold, and keep indemnified the Owner harmless from all actions, suits, claims, costs, fines, judgments and liabilities in respect of any matter or thing done or omitted to be done by the Sub-Contractors or their employees, workmen, representatives, agents, servants and suppliers in execution of or in connection with the work or arising out of or in any way alleged to be in connection with sub-contractors' performance under this contract, including but not limited to, not meeting the project milestones, non-compliance with the applicable laws and regulations of the government and local authorities, not obtaining the relevant licenses and permits, infringing any patents rights and specifically regarding the storage, use or disposal by the sub-contractors of hazardous materials in, on or under the Site or at any location whatsoever in connection with the project in any way. The sub-contractors' responsibility under this indemnification shall also include any and all hazardous materials introduced to the Site by their agents, representatives, employees, workmen, servants and suppliers. The obligations of sub-contractors under this clause survive till the closure of defects liability period.

35. CORRECTION OF WORK BEFORE VIRTUAL COMPLETION OF WORKS: The Estate Manager and the project consultant shall jointly conduct an extensive inspection just prior to the virtual completion of the work and shall prepare a list of materials, equipment, and workmanship which are defective or damaged or of substandard quality or improperly executed or generally unacceptable due to not being in conformity with the requirements stipulated in the contract documents. The vendor shall promptly remove, replace, re-execute, rectify and make good, to conform to the requirements stipulated in the contract documents and to the satisfaction of the Estate Manager and the Owner’s representative all such materials, equipment, and/or workmanship included or itemised in the said list and the vendor shall bear and pay for all expenses in connection therewith and consequent thereon and incidental thereto, including the cost for all remedial work on the work of other contractors destroyed or damaged by such removal, replacement, re-execution, rectification and making good. If the vendor fails to remove, replace, re-execute, rectify and make good the rejected materials, equipment, and/or workmanship within a reasonable time, fixed by written notice, the Owner may employ and pay other persons or agencies to carry out such removal, replacement, re-execution, rectification and making good and all expenses incurred in connection therewith, including all damages, losses and expenses consequent thereon and incidental thereto shall be recovered from the vendor and shall be deducted by the Owner from the contract price or any money that may be payable or that may become payable to the vendor.

36. LIQUIDATED DAMAGES / PROGRAMME CHART / MILESTONES: Subject to the provision penalty clause , any unexcused delay by the supplier in maintaining its contractual obligations towards delivery of goods and performance of services shall render the supplier liable to any or all of the following sanctions:

- deduction of liquidated damages amounting to a sum of  0.5% of the total contract price of the delayed/undelivered stores/services mentioned above for every week of delay or part of a week, subject to the maximum of 5% of the value of purchase order value..

- forfeiture of its performance security and termination of the contract for default

37. PENALTY / FINE:

37.1 Non Compliance to Safety codes: If the Estate Manager notifies the vendor of non-compliance with safety codes, the vendor shall immediately if so directed or in any event not more than 12 hours after receipt of such notice, make all reasonable effort to correct such noncompliance.

37.2 Levy of penalty/ fines: Levy of fines-consumption of  pan, gutkha, tobbacco, alcohol, drugs, etc is strictly prohibited on-site. Violation of this shall imply an immediate penalty of Rs.10,000.00 per instance and twice the amount there after post 3rd instance, Owner reserves the right the terminate the contract without further notice. If the vendor fails to do so, the Estate Manager shall have authority to levy penalty/ fines as may be determined based on the severity of the violation. The Estate Manager shall establish the list of violations and the fines associated with non-compliance of the safety codes. Each such non-compliance shall be treated as a breach of the contract.

37.3 Penalty : If the vendor fails to complete the work as per committed schedule, there shall be a penalty as per above clause.

37.4 Delay : In case the delay is not acceptable to the Owner, Owner reserves the right to terminate the contract and enter into fresh contract with other agencies at the cost of defaulting agency.

38. GUARANTEES:

i. The vendor understands and agrees that the Owner is expressly relying and will continue to rely on the skill and judgment of the vendor in executing the work and remedying any defects in the work. The contract represents and warrants that (i)  it shall perform the work in a timely manner, in strict accordance with the contract documents, and consistent with generally accepted professional, construction and construction-supervision practices and standards provided by an experienced and competent professional vendor  and construction supervisor rendered under the same or similar circumstances, and (ii) it is and will be responsible to the Owner for the acts and omissions of all sub-contractors and their respective employees, agents and invitees and all the persons performing any of the work.

ii. Besides the guarantees required and specified elsewhere in the contract documents, the vendor shall in general guarantee all work executed by the vendor. Those parts of the work or equipment or installations, for which extended guarantee periods are stipulated elsewhere in the contract documents, shall be guaranteed for such periods that are so stipulated. The duration of the defects liability period, unless specified otherwise, shall be the extent of length of such guarantee periods.

iii. The vendor represents, warranties and guarantees to the Owner, inter alia that:

•    The construction of the Project shall be approved and would be capable of use, operation, performance

and maintenance for accomplishing the purpose for which it has been built and acquired.

•    The work shall comply with the specifications, drawings, and other contract documents.

•    The work shall, for a period of 14 months from the date of issue of the virtual completion certificate.

which should be free from all defects and the project shall be of structural soundness, durability, ease

of maintenance, weather tightness etc.

•    The electrical materials, workmanship, fabrication and construction shall be of specified and

agreed quality and all materials shall be new.

•     The work performed for the Owner shall be free from all liens, charges, claims of whatsoever nature

from any party other than the Owner.

iv. Where, during such guarantee periods as mentioned above, any material or equipment or workmanship

or generally any item of work fails to comply or perform in conformity with the requirements

stipulated in the contract documents or in accordance with the criteria and provisions of the

guarantee, the vendor shall be responsible for and shall bear and pay all costs and expenses for

replacing and/or rectifying and making good such materials, equipment, workmanship, and items of

work and, in addition, the vendor shall be also responsible for and shall bear and pay all costs and

expenses in connection with any damages and/or losses suffered as a consequence of such failure.

v. All guarantees required under the contract shall be in the format approved by the Owner and submitted

to the project consultant and the Owner by the vendor when requesting certification of the final bill.

39. PROJECT CLOSE-OUT DELIVERABLES:   The vendor shall be responsible to provide all the

Project closeout deliverables as per the tender documents, prior to submitting its final bill. Such

deliverables shall include but not be limited to : -

i.  As-Built Drawings

ii. O&M Manuals;

iii. Guarantees/ Warrantees;

iv. Special warranties;

v. Extra material/ Attic stock;

vi. Operations Training for the Facilities Management staff of the Owner;

vii. Statutory approvals;

viii. Testing and commissioning reports;

ix. Contact list;

x. Handing over/ taking over certificate duly accepted by Owner.

40. DEFECTS LIABILITY:

40.1 Maintenance by vendor during Defects Liability Period: All defective items of work and defects noticed and brought to the attention of the vendor during the defects liability period shall be promptly and expeditiously attended to and replaced and/or rectified and made good by the vendor at its own cost, to the complete satisfaction of the Estate Manager and the project consultant.

40.2 Replacement and/or rectification and making good by vendors of all defective materials, equipment and/or workmanship during defects liability period: The vendor shall replace and/or rectify and make good, at its own cost, and to the satisfaction of the Estate Manager and the Owner’s representative, all defective items of work and defects arising, in the opinion of the Estate Manager, from materials, equipment, and/or workmanship not performing or being in accordance with the drawings or specifications or the instructions of the Estate Manager and or other contract documents or the best engineering and construction practices, and which may appear or come to notice within 12 months after virtual completion of the work, that is within the defects liability period as per the following :

i. Any item, material or matter repaired or replaced shall receive a new defects liability period of the same duration (12 months) beginning upon the date on which the said item is repaired or replaced , material or matter is returned for use to the Owner, provided that the aggregate guarantee period shall not be less than 12 months.

ii. The vendor shall be also liable for all costs associated with damages and/or losses which are a consequence of such defective items of work and defects, and such costs shall be recouped by Estate Manager from the vendor and shall be recovered from the retention money held and/or from the vendor's final bill (if the final bill has not been certified and paid for at the time).   Such defective items of work and defects as mentioned above shall, upon instruction and direction in writing of the Estate Manager and within such time as shall be specified therein, be replaced and/or rectified and made good by the vendor at its own cost.

iii. In case of default or failure by the vendor to replace and/or rectify and make good such defective items of work and defects, the Owner may employ and pay other persons or agencies to replace and/or rectify and make good such defective items of work and defects, and all costs, damages, losses and expenses therefore, consequent thereon and incidental thereto shall be to the account of the vendor and such costs, damages, losses, and expenses shall be recouped by the Owner from the vendor and shall be recovered from the retention money held and/or from the vendor's final bill (if the final bill has not been certified and paid for at the time).

iv. Should the retention money held (and the amount in respect of the final bill if it has not been certified and paid for at the time) be insufficient to meet such costs, damages, losses and expenses, as determined by the Estate Manager and project consultant, the vendor shall be legally bound to pay the balance amount due under the claim to the Owner within one month of receiving notification to that effect from the project consultant and Estate Manager. In the event of failure on the part of the vendor to pay the balance amount due within one month as stated above, the Owner shall be entitled to invoke the performance bond and the vendor shall raise no objection in this regard.

v. In respect of those parts of the work for which longer guarantee periods are stipulated elsewhere in the contract documents, the defects liability period for such parts of the works shall be until the end of the respective guarantee period that is stipulated for each such part.

41. FINAL COMPLETION OF THE WORK:  The work shall be considered as finally complete at the end of the defects liability period subject to the vendor having replaced and/or rectified and made good all the defective items of work and defects in accordance with clause above, to the satisfaction of the Estate  Manager, project consultant, Owner and provided that the vendor has performed all its obligations and fulfilled all its liabilities under the contract, and when the Estate Manager has certified in writing that the works are finally complete. Such final completion in respect of those parts of the project for which extended guarantee periods are stipulated elsewhere in the contract documents, shall be achieved at the end of such stipulated guarantee periods.

42. FORCE MAJEURE:

42.1 The right of the vendor to proceed with the work shall not be terminated because of any delay, subject to the time limits set forth in this clause, in the execution of the work due to unforeseeable causes beyond the control and without the fault or negligence of the vendor, or the sub-contractors, being Acts of God or that of the public enemy, act of terrorism restraints of Governing States, fires and floods. The following events are explicitly excluded from Force Majeure and are solely the responsibilities of the non-performing party: a) any strike, work-to-rule action, go-slow or similar labour difficulty (b) late delivery of equipment or material (unless caused by Force Majeure event), (c) economic hardship and (d) changes in applicable laws.

42.2 If the vendor is wholly prevented from the performance of the contract for a period in excess of thirty (30) consecutive days because of a Force Majeure, the Owner may terminate this contract by fifteen (15) days written notice delivered to the vendor, and if the period of the Force Majeure exceeds one hundred and twenty (120) consecutive days, the vendor may terminate this contract by fifteen (15) days written notice to the Owner.  In the event this contract is so terminated, the vendor shall be paid for the costs of the work actually executed up to the date of termination as certified by the Estate Manager.  Such costs shall not include loss of profits or for any other expenses of the vendor or sub-contractors such as salaries or wages of the employees or workers, hire charges for plant and machinery, expenses towards maintenance of establishment, demobilization, break charges or any other expense.  Failure to agree on an equitable settlement shall be deemed to be a dispute under this contract.

43. TERMINATION OR SUSPENSION OF THE CONTRACT BY THE OWNER:

43.1 If the vendor shall be adjudged bankrupt or if he should make a general assignment for the benefit of its creditors, or if a receiver shall be appointed on account of its insolvency /bankruptcy, or if he should persistently or repeatedly refuse to carry out the works diligently, or if he should fail to provide enough skilled workmen or materials or equipment or plant and machinery or tools or anything else necessary for the progress of the work in accordance with the approved construction programme, or if he should fail to make prompt payments to sub-contractors or to suppliers for materials or equipment or to its workers, or if he should persistently disregard laws or ordinances of the Central / State or local governments or disregards the instructions of the Estate Manager or the Owner’s representative, or if he should be guilty of a violation or breach of any provision of the contract, or if he has abandoned the contract, or if he has failed to commence the work within the time specified or if he has suspended the work, then the Owner, may without prejudice to any other right or remedy, and after giving the vendor seven days notice in writing, terminate the contract and take charge of all materials, equipment, tools, and plant and machinery thereon and use these as the Owner’s property for the completion of the project. In such case the vendor shall be entitled to receive any payment for the work completed by him only after the project is completed. If the amount due to the vendor for the work carried out by him as per the contract terms exceeds the expenses incurred by the Owner, including for additional management and administrative services, for completing the project and in respect of the damages and/or losses suffered by the Owner due to the vendor's default, then such excess shall be paid to the vendor within three months of the final completion of the project. If such expenses for completing the project and in respect of the damages and/or losses suffered by the Owner exceed the amount due to the vendor, then the vendor shall pay the difference to the Owner within one month of receiving the a notice to that effect from the Estate Manager or the Owner’s representative. The expenses incurred by the Owner for completing the work and in respect of the damages and/or losses suffered by him due to the vendor's default, shall be certified by the Estate Manager and its decision on this matter shall be final and binding on the vendor.

43.2 The Owner may terminate the work for convenience at any time for reasons other than for cause, without prejudice to any claims that the Owner may have against the vendor, by giving the vendor at least seven days’ prior written notice thereof. In such event, the Owner shall pay the vendor for such portions of the work as are completed and properly invoiced under the provisions for final payment as per tender clause  hereof for work performed prior to termination. In no event, shall the total payments made to the vendor exceed the contract price, and, prior to full payment, the vendor shall comply with the requirements for the release of claims and other documentation as appropriate as provided for under the provisions for final payment as per tender clause hereof. The Owner’s sole liability to the vendor for termination pursuant to the  tender clause shall be determined in accordance with the tender clause only and the vendor shall not be entitled to any further payments, including without limitation, loss of anticipated profits.

43.3 The Estate Manager or project consultant may suspend at any time and for any reason any part of or the whole of the work by giving at least 24 hours’ written notice thereof to the vendor, specifying the part of the work to be suspended and the effective date of such suspension. The vendor shall cease work on said part of the work on the effective date of such suspension but shall continue to perform any unsuspended part of the work.   During a suspension, the vendor shall only be reimbursed for the cost of the unsuspended work related to (a) the vendor’s employees whose work has been approved by the Estate Manager, and (b) such other items authorized by the Owner pursuant to a change order. The Owner may, at any time, authorize resumption of the suspended part of the work by notifying the vendor of the part of the work to be resumed and the effective date of suspension withdrawal. The work should be properly resumed by the vendor after receipt of such notice. The Owner’s sole liability to the vendor for suspension shall be determined in accordance with this clause and any approved change order, and the Owner shall not be liable for any other damages, including without limitation, loss of anticipated profits.

44. INTELLECTUAL PROPERTY RIGHTS:

44.1 It is hereby acknowledged and agreed that the Owner has commissioned the work in connection with the project and accordingly ownership of all intellectual property rights, including but not limited to property rights in the design and in all drawings, specifications and documents prepared by the project consultants, the vendor and any sub-contractors or vendors belongs and shall be assigned solely to the Owner who shall be entitled to deal with the designs, drawings, specifications and documents in whole or in part, in any manner in the Owner's sole discretion. The vendor hereby disclaims any right what so ever on these intellectual property rights in which cases the Owner shall be duly informed in that regard. This intellectual property right entitlement shall extend to any maintenance, repair and renewal, reinstatement and enlargement of the project. The vendor shall ensure that any provisions of this type necessary to protect the intellectual property rights of the Owner are included in all its contracts with sub-contractors.

44.2 All communications, whether written or oral, including but not limited to this contract, its annexure, drawings, data sheets, specifications, bills of material, sketches, calculations, designs and all other materials shall be treated as confidential and shall be the exclusive property of the Owner unless otherwise agreed in writing and must be given to the Owner upon request, but in any event all such materials shall be delivered to the Owner upon termination/expiry of this contract.

44.3  The contractor agrees that it and its employees, agents, sub-contractors and consultants shall not (without the prior written consent of the Owner) during the term of this contract or thereafter, disclose, make commercial or other use of, give or sell to any person, firm or corporation, any information received directly or indirectly from the Owner or the project consultant or acquired or developed in the course of the work, project or this contract, including by way of example only,  ideas,  inventions, methods, designs, formulas, systems, improvements, prices, discounts, business affairs, trade secrets, products, product specifications, manufacturing processes, data and know-how and technical information of any kind whatsoever unless such information has been publicly disclosed by authorised officials of the Owner. The vendor agrees that prior to assigning any employee or agent or hiring any sub -contractor or consultant to work on this project, such employee, agent, sub-contractor or consultant shall be required to execute a document containing in substance and form, a confidentiality provision similar to this provision.

44.4 The Vendor shall not, without the Owner's prior consent:

•  take any photographs or videos of the project (or any part thereof) for use otherwise than in connection

with carrying out and completion of the project;

•  write for publication, or cause, information or comment or pictures about the project;

• supply to any third person such as actual and prospective Owners, contractors, publishers, other

interested parties and the like, the designs and any articles or information relating to the project; and

• give interviews to the press including television, radio print and the like regarding the project or the

vendor’s involvement in the work.

44.5 Notwithstanding the foregoing, this provision shall not limit the obligation of the vendor to take photographs and/or videos on a regular basis for the purpose of providing the progress reports required by this contract.

44.6 The vendor, sub-contractors and their respective employees, representatives, agents, servants, workmen and suppliers shall not, during or after the termination/expiry of this contract, disclose any information pertaining to this contract or the project to any person without the prior written consent of

the Owner except when called upon to do so by a valid and lawful direction or order of a statutory or Government authority or an order of a court of law or where any of the parties require production of this document and related information for establishing their respective legal rights.

45. SETTLEMENT OF DISPUTES / ARBITRATION:

45.1 All disputes and differences of any kind whatsoever arising out of or in connection with this contract whether during the progress of the work or after their completion shall be referred in writing by the vendor to the Owner’s representative, and the Owner shall within 10 days from receipt make and notify its decisions thereon in writing to the vendor..

45.2 Decisions, directions, clarifications, measurements, drawings and certificates with respect to any matter the decision for which is specially provided for by these or other special conditions to be given and made by the Owner’s representative or by the Estate  Manager are matters which are referred to hereinafter as exempted matters and shall be final and binding upon the vendor and shall not be set aside on account of non-observance of any formality, any omission, delay or error in proceeding in or about the same or on any other ground or for any reason and shall be without appeal. They shall be specifically excluded from the scope of arbitration proceedings hereinafter referred to. In case of any ambiguity/dispute in arising out of or related to(including the  interpretation of any of the clauses in this tender document/purchase order/contract, decision of the Director IUCAA or his nominee shall be final and binding on all parties.

45.3 Subject to the aforesaid in the event of any dispute or difference between the parties hereto as to the construction or operation of this contract, or the respective rights and liabilities of the parties on any matter in question, dispute or difference on any account or as to the withholding by the Owner of any certificate to which the vendor  may claim to be and entitled to or if the Owner fails to make a decision within the aforesaid time, then and in any such case, but except in any of the exempted matters referred to in the above clause, the vendor after 90 days of its presenting final claim on the disputed matters, may demand in writing that the dispute or difference be referred to and settled by a sole arbitrator mutually acceptable to the Owner and the vendor. In the event the parties fail to appoint a mutually acceptable arbitrator, the parties shall approach the appropriate court for appointment of the sole arbitrator. The award of the Arbitrator, shall be final and binding on both the parties. The provision as per the Arbitration and Conciliation Act 1996 shall apply to such arbitration. The arbitration venue shall be at Pune. The procedure for the arbitration shall be determined by the arbitrator. Costs of such arbitration shall be equally shared between the Owner and the vendor.

45.4 The vendor shall not, except with the consent in writing of the Owner, the project consultant, in any way delay the carrying out of the work by reason of such matter, question or dispute being referred to arbitration but shall proceed with the work with all due diligence and shall, until the decision of the arbitrator is given, abide by the decision of the project consultant and no award of the arbitrator shall relieve the vendor of its obligations to adhere strictly to the Owner, the Owner’s representative’s or the Estate Manager’s instructions with regard to the actual carrying out of the work except as specifically affected by such award.

46. GOVERNING LAW: The governing law of the contract shall be Indian law. Any disputes related or arriving out this agreement shall be subject to the exclusive jurisdiction of courts of Pune.

47.STANDARDS OF CONDUCT:

47.1 Maintenance of appropriate business standards the vendor, in performing its obligations under this contract, shall establish and maintain appropriate business standards, procedures and control, including those necessary to avoid any real or apparent impropriety or adverse impact on the interests of the Owner. The Owner will in no event reimburse the vendor for any costs incurred for purposes inconsistent with such policies.

47.2 Compliance with laws, rules and regulations: vendor represents, warrants, certificates and covenants that in connection with performance under this contract that:

i. It shall, and the work to be provided hereunder shall, comply with all applicable local, State, and Central laws, rules and regulations, including but not limited to those governing building constructions, environmental, safety of persons and property, Employees State Insurance, Workmen’s Compensation, Provident Fund and applicable industrial/labour laws, and  land development laws, rules and regulations.

ii. No services provided hereunder will be produced using forced, indentured or convicted  labour or using the labour of persons in violation of the minimum working age law in the country where the work are rendered;

iii. It shall comply with all laws regarding improper or illegal payments, gifts or gratuities; and vendor agrees not to pay, promise to pay or authorize the payment of any money or anything of value, directly or indirectly, to any person or entity for the purpose of illegally or improperly inducing a decision or obtaining or retaining business or any advantage in connection with this contract;

iv. It has not paid or provided and shall not pay, any gratuity for the benefit of any agent, representative or employee of the Owner other than in accordance with the Owner’s applicable policies; and

v. It has not, and shall not, engage in any sharing or exchange of prices, costs or other competitive information or take any other collusive conduct with any third party supplier or bidder in connection with the preparation or submission of any bid or proposal to the Owner or the negotiation of this contract.

vi. It will also comply with all rules and regulations of the Owner which may be in effect at the facility site regarding employment, passes, badges, smoking, fire prevention, safety and conduct or property. On

behalf of the Owner,  vendor shall request and monitor that any contractor, sub-contractors, vendors and each of their employees observe such.

48. Tender Validity : The tenders shall remain valid for acceptance for a period of 90 days (Ninety days) after the date of tender opening prescribed in the tender document. Any tender valid for a shorter period shall be treated as unresponsive and rejected.

49. Signing and Sealing of Tender  :  The vendor shall submit their tenders as per tender clause.

- The original copies of the tender shall either be typed or written in indelible ink and the same shall be signed by the vendor or by a person(s) who has been duly authorized to bind the vendor to the contract. The letter of authorization shall be by a written power of attorney, which shall also be furnished along with the tender.

- All the copies of the tender shall be duly signed at the appropriate places as indicated in the tender documents and all other pages of the tender including printed literature, if any shall be initialed by the same person(s) signing the tender. The tender shall not contain any erasure or overwriting, except as necessary to correct any error made by the vendor and, if there is any such correction, the same shall be initialed by the person(s) signing the tender.

iii. The vendor is to seal the original copy of the tender in separate envelopes writing the address of the purchaser and the tender reference number on the envelope. The sentence “NOT TO BE OPENED” before 08th September, 2015  (the vendor is to put the date & time of tender opening) are to be written on these envelopes.   The inner envelopes are then to be put in a bigger outer envelope, which will also be duly sealed, marked etc. as above. If the outer envelope is not sealed and marked properly as above, the purchaser will not assume any responsibility for its misplacement, premature opening, late opening etc.

The envelopes must be super-scribed with the following information:

a) Tender Reference Number    b) Due Date  c) Name of the Vendor  d) Signature & Seal of Vendor    e ) Date

Technical Specifications of 150 KVA & Scalable upto 200 KVA Modular Uninterruptable Power Supply (UPS) System

This document specifies the characteristics of 150 KVA & scalable upto 200 KVA Modular UPS systems, especially designed for the critical equipments.

1 - Area of application for the specification :

This technical specification relates to the supply and installation of  scalable, modular Uninterruptible Power System (hereinafter referred as UPS), with a rated power rating of 150 KVA, architecture which is based on parallelable real plug-in Power Modules of double conversion configuration for power supply to critical equipments.

The UPS will be based on IGBT (Insulated Gate Bipolar Transistor) technology and high frequency switching techniques, so as to allow the operation of applications with a particularly high crest factor.

The technical specification defines:

- Technical specifications of supply and installation procedures;

- Acceptance tests and service trials on the manufacturer’s premises;

- Details to be outlined when submitting a proposal.

The bidder must compile the proposal in strict compliance with this technical specification. Any changes to and/or deviations from the specified features must be clearly indicated in the proposal; where no deviations are stated, it will be assumed that all technical characteristics listed herein have been satisfied.

# 2 - Reference standards :

Unless otherwise specified, the solution will comply in full with the following standards:

- EN 62040-1 Uninterruptible power systems (UPS) - Part 1: General and safety requirements for UPS

- EN 62040-2 Uninterruptible power systems (UPS) Part 2: Electromagnetic compatibility (EMC) requirements;

- Standard EN 62040-3 - Uninterruptible power systems (UPS) - Methods of specifying performance and test requirements;

# 3 - Abbreviations :

For ease of readability, the following naming conventions has been adopted (in alphabetical order):

N		Generic symbol for connection to neutral system;

EMC		Electromagnetic compatibility;

IEC                   International  Electrotechnical Commission;

PF		Power Factor.

4 - General description of the uninterruptible power system :

The modular UPS should offer redundant N+1 architecture based on parallelable Real plug-in power modules, incremental in steps.

Vertical modularity allows power scalability by simply plugging a power module into the existing modular system.

150 KVA to 200 KVA scaling required in a single chassis only.

Each power module should contain a full rated IGBT based rectifier and inverter, battery charger to charge the battery, logic controller, PFC & static switch.

## 4.1 - General characteristics :

Reference ambient conditions

- Nominal temperature range: 0° to +40(C

- Maximum relative humidity: 95% at ambient temperature, without condensation

The UPS must satisfy the following essential technical requirements:

| Number of Power Modules per system | As per OEM |
| --- | --- |
| Type of power supply (input/output) | 3ph + N / 3ph + N |
| Rated Output Power (Pn) | As per available |
| Input voltage and tolerance | 400 V, + 15%, -20% at 100% Pn |
| Input frequency and tolerance | 50 Hz +/-10% |
| Output voltage and tolerance | 400 V +/-1% sinusoidal |
| Output frequency and tolerance | 50 Hz ±0.05% (in free running) |
| Sound pressure measured at a distance of 1 m with rated load | < 80 dBA |
| Classification (CEI EN 62040-3) | VFI - SS – 111 |

Protection against direct contact with the UPS door open must be no less than IP20.

## 4.2  Plug-in power modules :

Power modules shall be:

- hot-swappable;

- pluggable or removable with the system working in double conversion (on line mode) mode without switching to bypass;

- There should be multi controllers to control all the modules;

- capable to detect automatically the variation of configuration (removal or insertion of modules) to share equally the load power according to the new condition (self-setting);

- static bypass module shall be present in each power module.

Power Modules:

- To meet above requirement, the system shall be comprised of power modules and shall be capable of being configured for N+1 redundant operation at the rated system load. Each power module should contain a full rated IGBT based rectifier and inverter, battery charger to charge the battery.

- The power modules should be independent and self sufficient modules without any centralised controller. The controller should be an integral part of power modules & rack. Failure of controller should affect only the respective power module and not the entire system.

- Selective disconnection: In case of Power Module failure, it shall be able to disconnect itself from the parallel working with the other power modules without compromising the load supply.

## 4.3 - IGBT rectifier :

The UPS rectifier must be the IGBT type throughout, with digital control of the DSP (Digital Signal Processor).

| Nominal voltage | 400V 3ph+N |
| --- | --- |
| Voltage tolerance | +15%, -20% at 100%Pn (without use of batteries) |
| Frequency | 50 Hz, +/-10% |
| Input power factor | ≥ 0.99 |
| Total harmonic distortion (THDi) | ( 3 % without active or passive filters |

To avoid resonance and slow response of protective devices, no active or passive filters to be used.

## 4.4 - IGBT battery charger :

The system must include a battery charger:

- with IGBT technology;

- dedicated and independent for each array of batteries;

The battery charger must be able to operate with the following types of battery:

- Sealed lead acid (SMF)

- Continuous monitoring of battery charger output voltage to keep it within the limits acceptable for battery life. Charge voltage fault warnings and deactivation of the charger;

- Residual battery capacity display.

## 4.5 - IGBT Inverter :

The inverter will be equipped with an IGBT switching circuit (PWM type) with the function of converting the rectifier or battery DC current to AC, and an output filter rated to generate the output voltage envelope. The inverter will be digitally controlled (DSP).

The inverter must be able to provide the nominal power at nominal current and voltage, with the following output characteristics:

| Stable voltage in static operation with input within allowable limits and load variation from 0 to 100% | ( 1% Vn |
| --- | --- |
| Stable voltage in dynamic operation with input within admitted limits and load variation from 0 to 100% and vice-versa | Compliance with IEC/EN 62040-3 Class 1 (VFI-SS-111) |
| Distortion of voltage waveform at rated linear load | ≤1% |
| Distortion of voltage waveform at rated non-linear load as per IEC/EN 62040-3 | ≤3% |
| Phase/neutral short circuit capacity in the event of mains failure for 330ms | 300% |
| Phase/phase short circuit capacity in the event of mains failure for 1s | 300% |
| Overload capacity for 10 min | For load 115% |
| Overload capacity for 60 seconds | For load 135% |

The inverter should be equipped with its own electronic output current-limiting circuit, so that components will not be damaged in the event of a short-circuit.

In the case of UPS units configured in parallel, the inverter should be protected by a combination of electronic circuitry and fuses.

The system will indicate the following situations affecting the inverter:

- general maximum temperature warning, with subsequent shutdown of the machine;

- uncoupling of frequency generator from auxiliary power source;

- tripping of power circuit fuses.

## 4.6 - Automatic bypass :

Static Bypass:

A fully rated (i.e. static switch of rating of power module) static bypass need to be provided along with the system. The static switch should be present in each power module.

The static switch shall be a naturally commutated high-speed static (SCR-type) device rated to conduct full load current continuously.

The static transfer switch control logic shall contain an automatic transfer control circuit that senses the status of the inverter logic signals and operating and alarm conditions. This control circuit shall provide an uninterrupted transfer of the load to an alternate bypass source without exceeding the transient limits specified herein, when an overload or malfunction occurs within the UPS or to bypass the UPS for maintenance.

Uninterrupted Transfer :

The transfer control logic shall automatically turn on the static transfer switch, transferring the critical AC load to the bypass source, after the transfer logic senses any of the following conditions:

- Inverter overload capacity exceeded.

- Critical AC load overvoltage or under-voltage.

- UPS fault condition.

The transfer control logic shall inhibit an automatic transfer of the critical load to the bypass source if any of the following conditions are present:

- Bypass frequency out of limits

- Bypass out-of-synchronization range with inverter output

4.7- Maintenance Bypass :

The manual bypass switch will be provided internally and must ensure that equipment downstream of the UPS is supplied directly by the UPS upstream power source, when rectifier, inverter and static switches are open. Switching to manual bypass and back should be possible without load supply interruption (Make Before Break).

4.8 - Reverse Phase Sequence Protection :

In the event of Phase sequence reversal at the input, UPS system shall continue to work on the main power supply and shall not trip the UPS system. Wrong phase rotation on the input of the converter ( rectifier) shall not stop the inverter neither switching the UPS into battery mode.

# 5 - Compliance with standards :

The system must comply with:

- Safety: EN EN62040-1 compliant.

- EMC emission: EN EN62040-2 compliant C2 class.

- EMC Immunity: EN62040-2 compliant C2 and C3 class.

# 6 - User interface, controls and warnings :

User interface

The onboard user interface must comprise a graphic display of 4 menu navigation buttons, multi-coloured LED status indicator with the following construction -

- The high-visibility screen must have protection against accidental impact.

The interface must enable the following commands/visual representations:

- Display of following values:

  - input and output voltages;

  - input and output currents;

  - input, output and control frequency;

  - battery voltage;

  - apparent and active power;

  - output load

Signals via terminal block contacts :

Built-in dry contact interface for electrical remote monitoring of UPS status.

- General Alarm;

- Load on Battery;

- Battery Low;

- Load on auto by-pass;

The following input commands must be available on the terminal block:

- E.P.O. (Emergency Power Off)

Remote Communication :

The UPS integrates network management functionality to enable supervision of the UPS by connecting it directly to the LAN. On board SNMP adapter allows the UPS to be monitored over networks as a peripheral. The adapter sends out traps on UPS alarms that can be monitored using Network Management Software or via web browser. It can be used in conjunction with a JNC client to perform an ordered shutdown of critical and virtual servers within the organizations  network.

The following communication protocols must be supported:

- SNMP agent and web server implemented in UPS supporting the following protocols: ARP, IP, ICMP, SNMPv1, SNMPv3 USM, UDP, TCP, HTTP, FTP, TFTP, SMTP, BOOTP, SNTP, DN and Telnet.

- Security login by MD5.

- User level management.

- Firmware upgrade for new features through TFTP.

- Batch configuration through FTP.

- Save event logs and history values of UPS in EEPROM.

- Scheduled UPS shutdown, restart and test.

- Wake-On-LAN packet to wake up PC.

- Send e-mail and SNMP trap to notify users.

- Provide JNC software to protect public operating systems.

Programmable Relay I/O Card :

- Status information on the UPS is presented as 6 contact closures and programmable output contacts.

- For back feed protection NC+NO auxiliary contacts required.

- UPS event monitoring in various application practices.

- Configurable UPS shutdown delay time.

- Configurable input signal during UPS shutdown or battery test.

- Provides gradual unattended shutdown to protect up to 6 computers.

MODBUS interface for BMS :

- MODBUS protocol over TCP/IP allows connection of the UPS to a network (Ethernet connection).

# 7 - Installation :

Following equipment delivery and installation, start-up procedures should be carried out by   engineers/technicians from the UPS manufacturer :

The following operations should be carried out at this stage -

- verification of regular system connection (positioning of and access to the UPS, mechanical inspection, environmental conditions, connections and protective devices, configurations);

- verification of the availability of required documentation;

- regular operation verification;

- validation of measurements taken during tests on the manufacturer’s premises;

- load test

- installation and verification of remote data transmission to the control station.

On completion of the commissioning procedure, the technician should deliver a full report of the service provided.

# 8 - Testing and Service trials :

The Client reserves the right to test the supplied units (UPS & Isolation transformer) on the manufacturer's premises. Client to be informed of the scheduled service trial date with at least seven days’ notice.

The test procedure, to performed at the company's expense and with a representative of the client (maximum 3 engineers) in attendance, will include the following steps:

- Documentation check

- Design, assembly and installation check

- Interconnections

- Instrumentation check

- Options description

- Synoptic panel description

- Rectifier static performance

- Battery and battery charger performance

- Static inverter regulation

- load test

- Inverter overload (with resistive load)

- Dynamic inverter regulation

- Bypass transfer test

All tests will be performed using appropriate instrumentation, accompanied by the relevant valid calibration certificates.

Isolation Transformer :

| Sr. No. | Parameter | Description |
| --- | --- | --- |
| 01 | KVA rating | 200 KVA |
| 02 | Impedance phase | 3-4% |
| 03 | Input voltage | 415V |
| 05 | Input/Output configuration | Delta/Star with zero seq filter |
| 06 | Construction | Copper Windings, Dry type, double wound, Air cooled, common core, varnish & Vacuum impregnated |
| 07 | Neutral conductor rating | 300% |
| 08 | Frequency | 50Hz |
| 09 | Insulation class/level | H/155°C |
| 10 | Maximum temperature rise | 155°C |
| 11 | Enclosure type | MS Enclosure as per IP21 |
| 12 | Enclosure finish | President Blue (RAL 5015) |
| 13 | Flash/HV test | 3 KV between winding to winding and winding to earth for 1 minute |
| 14 | Ambient temperature | 0 to +45 deg C |
| 15 | Operating humidity | 0 to 90% non condensing |
| 16 | Reference standard | UL-1561, IEEE-C 57-110, IS-11171 |
| 17 | "K" rating | K7 rating as per requirement with corresponding derating as per UL1561 and ANSI 57.110 guidelines. |
| 18 | Common Mode Noise Attenuation | 146 db (with triple shielding) |
| 19 | Suppression Joule Rating | 1190 Joules Total (1020 joules input / 170 joules output) |
| 20 | Noise Suppression Rating | 35-65 db |
| 21 | Audible noise | < 45-55 dBA at 1.5 m |
| 22 | Efficiency | > 95% |
| 23 | Load Regulation | Output maintained +/- 2% from nominal, from no load to full load |
| 24 | Overload | 1.17*In continuous, 3*In for 3 minutes, 3*In for 10 sec, 5*In for 1 cycle |
| 25 | Operating power factor | 0.75 lagging to 0.75 leading |
| 26 | Coupling capacitance | Within 5% no load to full load |
| 27 | Leakage current | Class “B” type |
| 28 | Dielectric strength | Standard 1:1 415V: 415V or 230V : 230 V |
| 29 | Tripplen Harmonics ampacity per phase (zero seq mitigation capacity) | 60% zero seq harmonics current of Rated Current capacity of neutrex (Load Current Tripplens Harmonics) |
| 30 | Tripplen attenuation in % | <5% (under 3 phase balanced load) |
| 31 | Continuous Over Current | 1.17 * In |
| 32 | Thermal overload | 1.17 * In |
| 33 | Transient Over Current | 1.2 * In FOR 3 MINUTE |
| 34 | Surge Test Conditions | Per ANSI/IEEE C62.41 - IEEE587 Cat. A & B test waveforms |
| 35 | Let-through Voltage (Ring Wave) | L-N: 20V L-G: 20V N-G: 0.5V |
| 36 | Let-through Voltage (Combination Wave) | L-N: 250V L-G: 250V N-G: 0.5V |
| 37 | Cooling Method | Natural Air Cooled |
| 38 | Input Isolator | Required |
| 39 | Output Isolator | Required |
| 40 | Metering | 1. DPM - at output with Resin case CT’s. EM6400 or equivalent with BMS interface 2. Temperature Indication with BMS interface |
| 41 | Indication Lamps & Alarms | 1.LED Type Phase indicators for both Input & Output 2. LED Type Fan failure alarm 3. LED Type Over temperature alarm & Buzzer. |
| 42 | Dry Contacts (Required for BMS) | 1. RS485 connectivity for the DPM & Temperature meter 2. Fan failure alarm 3. Over Temp alarm 4. Output Isolator position |
| 43 | Cable Entry | Top / Bottom |

UPS COMPREHENSIVE AMC CONTRACT

Scope Of Work :

- To efficiently maintain UPS by scheduled visit.

- To monitor & reduce various breakdowns by close supervision & preventive maintenance.

- To maintain UPS to get desired performance range

- To carry out proactive service of UPS in least downtime.

- To check log books & records maintained for each equipment by the customer& guide as necessary.

- To correct & repair minor faults/leakages to avoid breakdowns.

- To educate/train the operating maintenance staff for preventive maintenance.

- To attend Emergency/ breakdown calls on priority within 2 hours to provide workable solution.

- Breakdown calls  will not be charged in during contract period.

- Battery health report (Voltage & Internal Resistance of Batteries etc.) should be submitted to concern Incharge every month.

Mode of Operation :

- Your engineer will visit once in every month to UPS site to carry out preventive maintenance.

- Besides your Senior Engineers / Manager engineer will be visiting the site quarterly to confirm the activities & interact with our office for any feedback towards improvements in operation & handling.

- It is desired that a minimum inventory level, which will be mutually decided by us to be maintained at site to avoid delays & loss of down time.

- All tools & tackles required for the maintenance will be provided by vendor.

Termination of Contract : IUCAA  can terminate this contract by giving written notice not less than 30 days of service not found satisfactory.

Failure in Services :  In case of failure in providing satisfactory services by UPS Vendor, their products will be debarred in future procurement process.

Information as per format given below is to be furnished by the tenderer in technical bid failing which offer will not be considered.

| Tender Specification | Tenderer’s Specification |
| --- | --- |
| Make | Numeric/APC/Socomec/Emerson or equivalent |  |
| Model No. | Vendor to specify |  |
| UPS Capacity | 150 KVA Scalable to 200 KVA |  |
| Classification | VFI - SS – 111 |  |
| Duty | Continuous operation |  |
| Number of Power Modules required per system | As per OEM |  |
| Rated Output Power (Pn) per module | As per OEM |  |
| Type of power supply (input/output) | 3ph + N / 3ph + N |  |
| INPUT |
| Input voltage and tolerance | 400 V + 15%, -20% at 100 % Pn |  |
| Input frequency and tolerance | 50 Hz +/-10% |  |
| Dual Input Feed (Mains & Aux Mains) | Required |  |
| Input Power Factor |  |  |
| At 25% Load | >0.98 |  |
| At 50% Load | >0.99 |  |
| At 75% Load | >0.99 |  |
| At 100% Load | >0.99 |  |
| Input THDi |  |  |
| At 25% Load | <6% |  |
| At 50% Load | <5% |  |
| At 75% Load | <4% |  |
| At 100% Load | <3% |  |
| Output |
| Output voltage and tolerance | 400 V +/-1% sinusoidal |  |
| Output frequency and tolerance | 50 Hz ±0.05% (in free running) |  |
| Stable voltage in static operation with input within allowable limits and load variation from 0 to 100% | ( 1% Vn |  |
| Distortion of voltage waveform at rated linear load | ≤1% |  |
| Distortion of voltage waveform at rated non-linear load. | ≤3% |  |
| Crest Factor | 3.5:1 |  |
| Overload | 115% for 10 minutes & 135% for 1 minute |  |
| BYPASS |
| Full Rated Static Bypass in each power modules | Required |  |
| Rated Voltage | 400 V |  |
| Voltage Tolerance | +/-15% (Configurable) |  |
| Rated Frequency | 50 Hz |  |
| Transfer time with inverter synchronous with bypass | No interruption |  |
| Transfer time with inverter non-synchronous with bypass | <=20ms |  |
| Maintenance Bypass | Required Inbuilt |  |
| POWER MODULE |
| Type | Hot Plug in/ Hot swappable |  |
| Weight | Vendor to specify |  |
| AC-AC Efficiency : |  |  |
| At 25% Load | >94.5 % |  |
| At 50% Load | >95.5% |  |
| At 75% Load | >95.5% |  |
| At 100% Load | >95.5% |  |
| Communication : |
| WEB/SNMP Interface | Required |  |
| Dry Contact Interface | Required |  |
| Emergency Power Off (EPO) | Required |  |
| Environment |
| Operating ambient temperature | 0-40 Deg Celsius |  |
| Relative Humidity | 95% RH |  |
| Acoustic Level at 1 m distance | < 80 dBA |  |
| Heat dissipation in BTU/h | Vendor to specify |  |
| CABINET |
| Dimensions (WXDXH) in mm | Vendor to specify |  |
| Weight (Empty Cabinet) | Vendor to specify |  |
| Colour | Vendor to specify |  |
| Degree of Protection | Better than IP20 |  |
| STANDARDS |
| Performance | EN 62040-3 (VFI-SS-111) |  |
| Safety | EN 62040-1/EN 60950-1 |  |
| EMC | EN 62040-2 |  |
| BATTERIES |  |  |
| Type of Batteries | 12 V, SMF VRLA Batteries |  |
| No. of Battery Strings required | 02 |  |
| Battery backup from each string @ 150 KW load at 0.9 PF & ECV of batteries should be 1.75 V per Cell | 10 min for each string |  |
| No. of Batteries in each string | Vendor to specify |  |
| AH Rating of battery in each string | Vendor to specify |  |
| Battery Rack with 40 mtrs uninyvin DC cable | Required |  |
| DC Isolator with each battery string within Battery Rack | Required |  |
| Battery Rack Size & Weight | Vendor to Specify |  |
| Monitoring on UPS | I/P ( voltage, current, frequency) , battery ( voltage, current, backup time), O/P ( voltage, current, frequency), Data log for minimum 500 event for all parameters, |  |
| Protection system : | Overload, short circuit, input low voltage, input over voltage, output over voltage, output low voltage, battery over charging, battery low voltage, input low frequency/high frequency. No single point failure is accepted. |  |
| Cooling : | Forced air cooling |  |

LIST OF APPROVED MAKES

| Sr. No. | Name of Item | Approved Make |
| --- | --- | --- |
| 1 | UPS & UPS Rack | SOCOMEC/APC/NUMERIC/EMERSON or equivalent |
| 2 | SMF Batteries 12 Volts | Panasonic/Numeric/Quanta |
| 3 | Wires / Cables | Finolex/RR Cables |
| 4 | MV Boards, MCCs | Arrow/Zenith/ CPRI Approved |
| 5 | MCB Distribution Boards | Legrand/ L & T |
| 6 | Moulded Case Circuit Breaker, MCB | Legrand/L & T/ Schneider/ L& T |
| 7 | Indicating Lamps | Legrand/ L & T |
| 8 | Fuses & Fuse bases | HPL/ L & T |
| 9 | Digital KWH Meters with RS 485 Ports | Legrand /L & T |
| 10 | Indicating / Measuring Instruments | Legrand/ L & T /Schneider |
| 11 | Terminals | Elmex/ Connectwell |
| 12 | Isolation Transformer | Powermatrix/Esennar |

SEAL & SIGNATURE OF THE VENDOR

FORM -I

# ( To be printed on letterhead )

# Undertaking

1.	I,  __________________________________________   son/ daughter/ wife of Shri.

_____________________________________________________________________

Proprietor/ Director/authorized signatory of the Company/Firm mentioned above, is competent to sign this declaration and execute this tender document.

- I have carefully read and understood all the terms and conditions of the tender and undertake to abide to them.

- The information/documents furnished along with the above tender form are true and authentic to the best of my knowledge and belief. I am well aware of the fact that furnishing of any false information/ fabricated document would lead to rejection of my tender at any stage besides liabilities towards prosecution under appropriate law.

Place : Pune                                                                                          Authorised Signotory

Sign and seal

Date

FORM -II

# ( To be printed on letterhead )

DECLARATION

Declaration letter on official letterhead stating the following:

- We are not involved in any major litigation that may have an impact of affecting or compromising the delivery of services as required under this tender.

- We are not black-listed by any Central/State Government/Public Sector Undertaking in India.

Yours faithfully,

(Signature of the Authorized person)

Date:	Name:

Place:	Designation:

Seal:

FORM -III

# ( To be printed on letterhead )

## EMD refund request form

To

Administrative Officer (Purchase)

Inter-University Centre for Astronomy & Astrophysics

Post bag -4, Ganeshkhind,

Pune University Campus,

Pune -  411007.

Sub :- Request for refund of EMD deposited for tender for "Supply, Installation and commissioning

of UPS System at IUCAA, Pune.

Sir,

I/We request you that EMD deposited by me/us against the tender above tender due on                      08th September 2015 vide DD No                      dated             for Rs.1,00,000/- against tender for  "Supply, Installation & Commissioning of UPS System at IUCAA"  Pune  may kindly be refunded.

Yours faithfully,

For M/s. ___________

(Signature & Seal)