Minutes

July 24, 2012

PRE-BID MEETING – FOR L.T ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK AT IUCAA.

The Pre-bid meeting for LT electrical works for new data centre, residential and hostel block at IUCAA was held on July 24, at 1500 hrs in the office of Administrative Officer (Purchase). The following members were present:

- Mr. B.V.Sawant

- Mr. G.B.Gaikwad

- Mr. N.V.Nagrathnam - Consultant

There was only 1 representative from M/s. Suvarna Electricals, Pune who attended the meeting, the list of which is enclosed as Annexure – 2. The questions raised by the vendors and reply given from IUCAA is enclosed as Annexure -1.

All the vendors are content with the replies received from IUCAA and have confirmed that the scope of work requirement at IUCAA is clear to them along with the tender conditions mentioned therein.

The meeting concluded at 1545 hrs with vote of thanks.

B.V.Sawant                                             G.B.Gaikwad                                   N.V.Nagrathnam

Annexure – 1

Clarifications regarding points discussed with Mr. Prakash Patil, Sr. Manager of M/s.Suvarna Electricals  in Pre-Bid Meeting held on 24.07.12 at 1500 hrs in the office of Administrative Officer  (Purchase).

| Section | Section Name | Sr.No. | Tender Description | query | Reply to query |
| --- | --- | --- | --- | --- | --- |
| A | M.V.Switchgears and distribution boards | 1.1 | DTM Meter | Please mention the full form of DTM with required makes. Whether with RS 485 or not? | DTM - Dual Tariff Meter with CT's & RS 485 port. make- Trinity |
| A | M.V.Switchgears and distribution boards | 1.7 | S/g Panel - 1250A Copper busbar | Incoming & outgoing cables are Aluminium armoured. So please confirm the material (Aluminium/Copper ) for Busbar. | Aluminium Busbar only as indicated in SLD/BOQ. |
| B | Cable and Busduct | 4.3.6, 4.3.8, 4.3.9, 4.3.1.0 | Ceiling supports for 600mm width | As you have not mentioned the quantities it is very difficult for material supplier's to define the other accessories requirement/ quantities. So please mention your quantities. Also supports required are mentioned in Nos. , we request you to consider this point in Fabrication - item no. 4.4.1 | Vendor to quote for rate only as indicated in BOQ for cable tray sizes as follows: 1) 600 mm width x 54 mm depth 2) 450 mm width x 54 mm depth 3) 300 mm width x 54 mm depth |
| C | Earthing System | 1.1,1.2 | Copper / GI Plated electrode | Please mention the approved makes with contact details | Make - JEF as indicated in List of approved make. Contact details: Mr. Bhavik - 9049808887 email - bhavik@jeftechno.net |
| C | Earthing System | 2.5 | 32 x 5mm Tinned copper strip | 32 x 5 mm Size is not a std size. Please confirm with 30 x 5mm std. size. | 32 x 5 size is ok.& is available. |
|  | Completion period |  | Important note : completion period mentioned is 1 month | For item # 1.1,1.7,1.8 completion period will be one month after drawing approval from client. For item no. 3.1& 4.3 delivery period 8 - 9 weeks from drawing approval | For item no. 1.1, 1.7 & 1.8, 4-5 weeks completion period should include drawing approvals also. For item no. 3.1 & 4.3, 9-10 weeks delivery periods is ok.(including drawing approval) |

Annexure - 2