Tender for

TENDER FOR SUPPLY & INSTALLATION OF

2 x 320 KVA DG SETS

at

Inter-University Centre for Astronomy and Astrophysics

# Post Bag -4, Ganeshkhind, Pune University Campus,

Pune 411 007.

Bill of Quantities (BOQ)

&

Financial Bid

Financial Bid - Part  B

“TENDER FOR SUPPLY & INSTALLATION OF

2 x 320 KVA DG SETS”

THE INTER UNIVERSITY CENTER FOR ASTRONOMY & ASTROPHYSICS (IUCAA)

POST BAG 4, GANESHKHIND, PUNE UNIVERSITY CAMPUS,

PUNE 411 007, INDIA

Name of Work   : 	             			D.G.SET  –  AT IUCAA

A.	Name of Vendor  / Firm / Company		____________________________

____________________________

Postal Address				       	   ____________________________

____________________________

Telephone Off.					____________________________

Telex / Fax						____________________________

Email ID						____________________________

Signature & seal of Bidder

| SUMMARY OF COSTS FOR HT ELECTRICAL WORKS |
| --- |
| S. NO. | DESCRIPTION | AMOUNT (RS.) |
| 1.0 | DIESEL GENERATING SET |  |
| 2.0 | LOAD TESTING OF DG SETS |  |
| 3.0 | EXHAUST SYSTEM |  |
| 4.0 | DG FUEL SYSTEM |  |
| 5.0 | CABLES AND BUSDUCT : |  |
| 6.0 | EARTHING SYSTEM |  |
| 7.0 | DG AMF & Synchronising Panel |  |
| 8.0 | Charges for Laisoning & Sanction for the DG set |  |
|  | TOTAL |  |
| Note: | Amount in Words :- 1) Erection rate shall include receiving, unloading, storing, transportation, installation, testing and commissioning at site. 2) Estimated cost is inclusive of all taxes.( such as VAT, Octroi, WCT etc) |

Seal & Signature of the bidder

TENDER FOR SUPPLY & INSTALLATION OF 2 x 320 KVA DG SETS

| PROJECT : SUPPLY & INSTALLATION OF 2 x 320 KVA DG SETS AT IUCAA, PUNE |
| --- |
| BILL OF QUANTITIES FOR 2X320 KVA DG SETS |
| Sr. No. | Description | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
|  |  |  |  |  |  | Supply |  |
| 1.0 | DIESEL GENERATING SET |  |  |  |  |
|  | Design, manufacture, assembly, testing at works, supply, erection & testing at site as per specifications complete in all respect of DG Sets of 2 X 320 KVA rating as specified below: |  |  |  |  |
|  | 415 Volts, 3 phase 4 Wire, 50 Hz, 1500 RPM AC alternator coupled with Radiator Cooled Diesel Engine complete with all accessories, like self starting device, fly wheel coupling with guard, V belts, cooling system, instrument panel comprising of switch with key, starting battery & battery charging device, safety control for lub oil pressure with tripping etc. The alternator insulation shall be class 'H' with temperature rise limited to Class 'F' value suitable to withstand tropical conditions and shall generally comply with BS 5000 and IS 4722. The over load capacity shall not be less than 110% of rated capacity for 1 hour in every 12 hours. DG Set shall be enclosed in an acoustic enclosure. The enclosure shall have provision of space required for inspection and minor maintenance. 24 Volt Lead Acid rechargeable battery set of adequate AH rating complete with teak wood battery stand, suitable trickle/boost chargers, battery leads. Neutral CT of suitable ratio & Class PS accuracy mounted in the terminal box for Alternator REF protection shall be included. |  |  |  |  |
|  | The DG set shall be mounted on a suitable designed fabricated rigid common base frame with antivibration pads to provide not less than 99% vibration isolation. First filling of lube oil & HSD shall be included in DG Sets cost. The DG Set shall include all standard accessories, fittings, instruments and 3 sets of operating & maintenance manuals, spare parts list etc. complete as per technical specifications. The DG set shall be inclusive of AMF controller as per item no. 6.1, Fuel day oil tank as per item no. 4.1, Silencer as per item no. 3.1 etc. complete as required |  |  |  |  |
|  | The design of DG Sets shall conform to the requirement of CPCB for all parameters including flue gas emission and noise level. DG set should be provided with standard accessories like anti vibration pads, AVR, electronics governor, breaker, MFM, control cables, power cables complete as required up to AMF panel. BMS compatible ports & I/Os. |  |  |  |  |
|  | BMS Requirement: |  |  |  |  |
|  | DG Vendor to ensure the BMS system architechture(as indicated in Annexture - 1 for reference only) shall be able to satisfy the client's requirement. Follwing are some of requirement listed for guidance but not limited to: |  |  |  |  |
|  | 1) RS 485 / Backnet Output from each DG set for our BMS |  |  |  |  |
|  | 2)Analog input along with monitor points for fuel level, generated voltage, current, engine temperature,radiator temperature, Battery voltage, changing current & over speed, winding temperature, RPM frequency etc. |  |  |  |  |
|  | 3) Potential free contacts from each DG set breaker for BMS for ON/OFF/Trip status |  |  |  |  |
|  | 4) BMS Controller with 5 Universal Inputs and 5 Binary Outputs in MS Enclosure with reqd power supply ,connecters,internal wiring |  |  |  |  |
|  | 5) Convertor with 2 inputs and 1 RS 232 output, cabling etc. |  |  |  |  |
|  | 6) Software for Graphical presentation |  |  |  |  |
| 1.1 | 320 KVA (with acoustic enclosure & standard accessories) comprising of atleast standard features & Accessories as follows: | Set | 2 |  |  |
|  | GENERATOR STANDARD FEATURES: |  |  |  |  |
|  | Vendor to provide one-source responsibility for the generating system and accessories. |  |  |  |  |
|  | The generator set and its components are prototype-tested, factory-built, and production-tested. |  |  |  |  |
|  | Two-year limited warranty covers all systems and components. |  |  |  |  |
|  | Industrial diesel engine with battery charging alternator. |  |  |  |  |
|  | Alternator with insulation class H. |  |  |  |  |
|  | Unit-mounted radiator with atleast 50 Deg.C . |  |  |  |  |
|  | Subbase fuel tank - 990 ltrs. Capacity with float type level indicator. |  |  |  |  |
|  | Vibration isolators. |  |  |  |  |
|  | Dry type air filter with restriction indicator. |  |  |  |  |
|  | Fuel Water separator. |  |  |  |  |
|  | Main line breaker. |  |  |  |  |
|  | Starting battery and cables. |  |  |  |  |
|  | Sound enclosure with 75dB(A). |  |  |  |  |
|  | Conveniently locate fuel level indication. |  |  |  |  |
|  | Operation and installation literature. |  |  |  |  |
|  | ALTERNATOR STANDARD FEATURES: |  |  |  |  |
|  | Alternator meets BS EN 60034 and the relevant section of other international standards such as BS5000, VDE 0530, NEMA MG1-32, IEC34, CSA C22.2-100, AS1359. |  |  |  |  |
|  | Self-ventilated and dripproof of IP23 construction |  |  |  |  |
|  | Superior voltage waveform form a 2/3 pitch wound stator. |  |  |  |  |
|  | ADVANCED DIGITAL CONTROL : |  |  |  |  |
|  | Compact Controller comprising of : |  |  |  |  |
|  | LED display: |  |  |  |  |
|  | Runtime hours |  |  |  |  |
|  | Current |  |  |  |  |
|  | Voltage |  |  |  |  |
|  | Frequency |  |  |  |  |
|  | Engine temperature |  |  |  |  |
|  | Engine Oil Pressure |  |  |  |  |
|  | Battery Voltage |  |  |  |  |
|  | LED display faults: |  |  |  |  |
|  | High engine temperature |  |  |  |  |
|  | Low oil pressure |  |  |  |  |
|  | Over crank |  |  |  |  |
|  | Overspeed |  |  |  |  |
|  | Over & under voltage |  |  |  |  |
|  | Over & under frequency |  |  |  |  |
|  | E-stop |  |  |  |  |
|  | Auxiliary fault |  |  |  |  |
|  | Display warning: |  |  |  |  |
|  | Low battery voltage |  |  |  |  |
|  | High battery voltage |  |  |  |  |
|  | Low fuel level |  |  |  |  |
|  | STANDARD FEATURES & ACCESSORIES: |  |  |  |  |
|  | Standard Features: |  |  |  |  |
|  | Master switch: Run/Off-Reset/Auto |  |  |  |  |
|  | Current selector switch |  |  |  |  |
|  | Remote two-wire start/stop capability |  |  |  |  |
|  | Event log |  |  |  |  |
|  | Superior electronics |  |  |  |  |
|  | Factory-built and production-tested |  |  |  |  |
|  | Automatic start with programmed cranking cycle |  |  |  |  |
|  | Field software upgrade possibility |  |  |  |  |
|  | Environmental specifications : |  |  |  |  |
|  | Operating temperature: --20oC to 70oC (--4oF to 158oF) |  |  |  |  |
|  | Storage temperature: --60oC to 70oC (--76oF to 158oF) |  |  |  |  |
|  | Humidity: 0--95% condensing |  |  |  |  |
|  | Power Requirements : |  |  |  |  |
|  | 12 or 24 VDC with fuse protection |  |  |  |  |
|  | 250 mA @ 12 VDC |  |  |  |  |
|  | 125 mA @ 24 VDC |  |  |  |  |
|  | Accessories: |  |  |  |  |
|  | Battery charger 12V/24V |  |  |  |  |
|  | Mains sensing relay |  |  |  |  |
|  | Earth leakage protection |  |  |  |  |
| 2.0 | LOAD TESTING OF DG SETS |  |  |  |  |
|  | The DG Sets shall be subjected to load tests at factory before despatch & IUCAA site after installation in the presence of Iucaa`s representative with consultant.All consumables required during testing of DG Sets at factory shall be included in the scope of DG vendor. All consumables required during trial run of DG Sets on load for 15 hours out of which one hour for run up to full load, followed by six hours on full load and concluded by one hour 110% overload capacity to be arranged by client. Also, client to arrange the Load availability for testing. The test shall be carried out as per Technical Specification & records to be submitted for approval.(The formats of all tests carried out at factory & at site with details of relevent standards as per latest standerds & permissible limits should be submitted by DG vendor for reference along with tender.All the arrangement of factory visit including stay-if required, shall be in the scope of DG vendor.) |  |  |  |  |
| 2.1 | 320 KVA | Set | 2 |  |  |
|  |  |  | Notes: |  |  |  |  |
| 1 | These DG Sets required to provide power to HPC Data centre which is very crucial & important facility needed 24 X 7 power & 99.99 % up time. |  |  |  |  |
| 2 | DG Set should accepts rated load in one step. |  |  |  |  |
| 3 | The Client/Consultants reserves the right for load testing on any/all of the DG Sets. |  |  |  |  |
| 4 | DG Sets panel shall be suitable for Auto operation controlled through AMF Relay as well as manual operation. |  |  |  |  |
| 5 | DG Set supplier shall provide microprocessor based DG Local Control panel mounted on the engine having, all electrical parameters, and fault indication with provision for its remote control. |  |  |  |  |
| 6 | DG Supplier should provide for all required hardware (convertor to give bacnet compability, control wiring, potential free NO/NC,RS ports,A/D & D/A converters etc. as required to operate the BMS system software.)arrangement for remote start/stop and DG fault (LLOP, over speed) etc along with remote adjustment of voltage & speed of the engine (Motorised/ solid state pot. may be required) & shall be included in the quoted rates as required. |  |  |  |  |
| 7 | The neutral CTs as per specification shall be provided on the neutral side of winding and connection brought out to a neutral CT box to be mounted on the alternators (All the six terminals are to be brought out and then shorted). |  |  |  |  |
| 3.0 | EXHAUST SYSTEM | Sets | 2 | Included in the above Item no.1 |
| 3.1 | Silencer |  |  |  |  |
|  | Supply, installation, testing & commissioning of residential type silencers as per CPCB norms with 75mm glass/ mineral wool insulation complete with wire chicken mesh and 24 guage Aluminium cladding from engine upto silencers, including supporting arrangement suitable for the following DG Set complete as required. |  |  |  |  |
| a | 320 KVA DG Set | Sets | 2 | Included in the above Item no.1 |
| 3.2 | SUPPORTING STRUCTURE FOR EXHAUST SYSTEM |  |  |  |  |
|  | Supply, Fabrication & Erection of M.S. steel structure made of M.S. angles / Channels etc. duly painted as required at site for DG exhaust pipe support. (For 2 Nos. DG sets) | Kg | 500 |  |  |
| 4.0 | DG FUEL SYSTEM |  |  |  |  |
| 4.1 | FUEL DAY OIL TANK |  |  |  |  |
|  | Supply, fabrication, installation, testing & commissioning of M.S. day oil tank of 990 litres capacity fabricated out of min. 2.5mm thick M.S. sheet installed on steel frame or masonry pedestal with all associated accessories, filters, valves & fittings including level controller, priming motor complete as required, float switch with contacts for remote interlock should be provided. The tank shall be suitably treated with oil resistant paint/anticorrosive treatment. The contact of level controller shall be wired up terminal block. | Set | 2 | Included in the above Item no.1 |
| 4.2 | Fuel Oil Piping |  |  |  |  |
|  | Supply, installation, testing and commissioning of schedule- B class MS piping conforming to IS-1239 for fuel piping complete with all necessary fittings and valves between day oil storage tanks and DG sets including jointing of pipes, painting with 2 coats of red oxide and two coats of enamel paint. |  |  |  |  |
| a) | 20 mm dia | RM | R.O. |  |  |
| b) | 25 mm dia | RM | 100 |  |  |
| c) | 50 mm dia | RM | R.O |  |  |
| 4.3 | Oil Hand Pump |  |  |  |  |
|  | Supply & installation of hand pump for pumping out fuel from barrels to the day oil tank with flexible hose pipe of 25mm dia x 25 mtr length & end coupling sockets etc. as required | No. | 2 |  |  |
| 5.0 | CABLES AND BUSDUCT : |  |  |  |  |
| 5.1 | Supply and laying in existing cable Trays/ Hume Pipes/clamped to wall with suitable clamps saddles and fixing bolts including testing and commissioning of the following 1100 volts grade armoured XLPE insulated and sheathed aluminium/copper conductor cable complete as required. Identification tags shall be provided for all cables. |  |  |  |  |
| A | Aluminium conductor |  |  |  |  |
| 5.1.1 | 4R x 3.5C x 300 Sq.mm AYFY | RM | 80 |  |  |
| 5.2 | Cable end termination of the following PVC copper/aluminium cables 1100 Volt grade including cost of crimping tinned copper heavy duty bimetallic lugs, double compression glands, insulation tape and all requisite material for completion of joints. |  |  |  |  |
| A | Aluminium conductor |  |  |  |  |
| 5.2.1 | 4R x 3.5C x 300 Sq.mm AYFY | No | 8 |  |  |
| 6.0 | EARTHING SYSTEM |  |  |  |  |
| 6.1 | Earthing Stations: |  |  |  |  |
|  | Supply, installation, testing and commissioning of eco safe electrical grounding system offering a stable grounding back fill compound for a long period of time. i.e It should be electrically conducting & not dependant on moisture & confirming to ANSI/NSF Standard 60, will not diffuse in to the ground, will not expand or experience any shrinkage but remain in constant contact with earth & should be able to reduce contact resistance to earth significantly(at least 40 %) & create a low steady state impedance for a very long period resulting in faster transient dissipation. The standard earth electrode shall be made of high tensile low carbon steel circular rods, molecularly bonded copper or clad copper on the outer surface to confirm with the requirements of UL467-2007; thus reducing earth resistance(i.e combined resistance of electrode & contact resistance between electrode & soil) as an alternating low impedance path for the dangerously high voltages in the electrical distributor system. Providing masonry enclosure with 10 mm thick C.I. cover plate having locking arrangement and disconnecting/ testing links etc as per IS –3043 complete as required. |  |  |  |  |
| 6.1.1 | With Copper plated electrode of 25 mm dia rod | Set | 10 |  |  |
| 6.1.2 | Soil resistivity testing & report | Location | 2 |  |  |
| 6.2 | Earthing Strip/Wires |  |  |  |  |
|  | Supply, installation, testing and commissioning of following sizes of GI/ Copper strip/ wire clamped to walls, cable trays, bus ducts, cables in recess or surface etc for equipment/ System earthing complete as required including inter connection between length at joints, all fixing accessories saddles, clamps etc and other fixing hardware material as required for proper installation. |  |  |  |  |
| 6.2.1 | G.I. Earthing strip/wire |  |  |  |  |
| a) | 50 x 6 mm strip | RM | 60 |  |  |
| b) | 32 x 6 mm strip | RM | RO |  |  |
| 6.2.2 | Copper earthing strip/wire |  |  |  |  |
| a) | 50 x 6 mm strip | RM | 40 |  |  |
| b) | 32 x 6 mm strip | RM | RO |  |  |
| 7.0 | DG AMF & Synchronising Panel |  |  |  |  |
|  | Design, manufacture, supply, installation, testing and commissioning of following MV switchgear panels suitable for 415 V, 3 phase, 4 wire, 50 Hz power distribution system. The panel shall be Indoor, wall/floor mounting, sheet metal clad, cubicle, dust and vermin proof type compartmentalised design fabricated out of 14 SWG sheet steel, complete with aluminium bus bars, separate earth bus bar to be provided through out the length of the panel along with base chanel of suitable size. The incoming and outgoing feeders shall be accommodated in a modular multitier arrangement, adequate size cable alley, painting, earthing, numbering, danger plate etc as required & as per specifications and drawings. Current density for busbar size shall be designed considering not more than 1.0 A/sq.mm current density for copper & 0.8 A/sq.mm for aluminium. The switchgear live parts shall be isolated with proper insulation material. The current transformer shall be cast resin type. IP - 54 protection for DB, panel for indoor & IP - 67 for outdoor DBs, panels or mentioned specifically & as follows: |  |  |  |  |
| 7.1 | Supply, Installation, Testing & commissioning of 1 MVA panel comprising of 4 incomers i.e. 4 no.s x 630 A, 36 kA, 4 pole, motorised MCCB (Legrand make Cat No. 025657) with earth leakage module 4pole (Legrand make Cat No. 026065),UVR 415 Volts,Sprader links(Legrand make Cat No. 625008) & 2 nos. outgoing 2000A, 4pole,EDO, microprocessor based ACB, with electromechanical interlock, 65 kA frame one (Legrand make Cat No. 028735)with Over load / Short Circuit / Earth Fault protection, 4 NO + 4 NC Aux. contacts , trip contact, & protection accessories viz. communication module (Legrand make Cat No. 028805), 12 Volts DC external power supply(Legrand make Cat No. 028806),Module programmable output(Legrand make Cat No. 028812), External neutral CT (Legrand make Cat No. 028811),Rear terminals(Legrand make Cat No. 028897), AMF unit, synchronising relay, auto load sharing relay & auto / manual selector switch, three phase sensing for mains & 2 phase 415 volt AC sensing for alternator aux. voltage 24 V DC with inbuilt protection UV, O/V, O/F for attenuator, low battery & high voltage protection, combined digital meter (A+V+Hz) 400 / 5 A 415 V AC, 4 wire & Aux. supply, KWH meter, electronic hooter, 24 V DC solid state annunciator. 12 window (6x2), 24 V DC including master trip relays, CTs, auto/manual selector switch, breaker control (trip/neutral/close), indicating LED lamps. Delay timer & battery charger with DC 0 - 50 voltmeter & 0 - 30 A DC ammeter, charger having 230 V incomer & 24 V DC 18 A o/p SMPS unit etc.indicator lamps as required(For 4 nos. x 630 kVA DG sets), Voltmeter/VSS/Control MCB - 2 Set, Ammeter/ASS/CT 2000/5A, 15 VA CL.1 -2 Sets,. Vendor to note that the panel should be extendable type to accomadate future DG's if required. | Set | 1 |  |  |
| a) |  |  | Incomer -1 |  |  |  |  |
|  |  |  | 630 A, FP MCCB(legrand- cat.no. 025657) 36 kA microprocessor release protection for LSIG. - 4 Nos. |  |  |  |  |
| b) | Incomer -2 |  |  |  |  |
|  | 1 no. ATS comprising of 2000 A, FP ACB (legrand- cat.no. 028735) 65 kA microprocessor release protection for LSIG. 2 Nos. with electromechanical interlock, Automation control communicating unit(legrand- cat.no. 026194) complete as required. |  |  |  |  |
| c) | Metering & Protection |  |  |  |  |
|  | Phase indicating neon lamps - 6 Sets |  |  |  |  |
|  | Voltmeter/VSS/Control MCB - 2 Sets |  |  |  |  |
|  | Ammeter/ASS/CT 2000/5A, 15 VA CL.1 - 2 Sets |  |  |  |  |
|  | Digital MFM meter (7 Parameters) with CT's - 2 Sets |  |  |  |  |
| d) | Busbar |  |  |  |  |
|  | 2500A, FP, 65kA, Al busbar insulated with colour coded heat shrinkable sleeves. |  |  |  |  |
| 8.0 | Charges for Laisoning & Sanction for the DG set |  |  |  |  |
|  | Statutory approval from authorities like PWD, SEB, CPCB etc. for installation & commisioning of above DG sets complete as required. Vendor to prepare & submit required documents & drawings to authorities for sanction & approval & submit the commissining report to the client. Please note that any statutory payment to the departments shall be paid by the clients seperately on submission of the receipt by vendor. | L.S | 1 |  |  |
| 9 | Annual maintenance Contract after Warranty Period: |  |  |  |  |
| Sr. No. | Year | Comrehensive AMC Costs in Rs. | Non Comprenhensive AMC Cost in Rs. |  |  |  |  |
| 1 | First Year |  |  |  |  |  |  |
| 2 | Second Year |  |  |  |  |  |  |
| 3 | Third Year |  |  |  |  |  |  |
| 4 | Fourth Year |  |  |  |  |  |  |
| 5 | Fifth Year |  |  |  |  |  |  |
|  | Total Rs. |  |  |  |  |  |  |
|  | GRAND TOTAL |  |  |  |  |
| Notes: The panel vendor to submit following details for approval: |
| a) Power SLD |
| b) Control wiring diagram |
| c) G. A. Drawing |
| d) B. O. M. |

| Lowest Cost Criteria |
| --- |
| Sr. No. | Particulars | Rs. |
| 1 | Basic cost of Generator Sets ( Supply & Installation) |  |
| 2 | Cost of AMC for 5 years after warranty period |  |
| 3 | Cost of DG set working at 80% for 2 hrs a day & 300 days per year for 5 years |  |
| 4 | Total Cost of ownership at the end of 5 years |  |
|  | Total AMOUNT |  |
| Total Amount in Rupees - Note : 1) The vendor should include relevant information in the blank space. 2) Cost of Diesel shall be considered at Rs. 50.00 per Liter SEAL & SIGNATURE OF THE BIDDER |