TENDER FOR LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK

at

Inter-University Centre for

Astronomy and Astrophysics

# Post Bag - 4, Ganeshkhind, Pune University Campus,

Pune - 411 007.

Technical Bid - Part  A

TENDER FOR LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK

THE INTER UNIVERSITY CENTER FOR ASTRONOMY & ASTROPHYSICS (IUCAA)

POST BAG 4, GANESHKHIND, PUNE UNIVERSITY CAMPUS,

PUNE 411 007, INDIA

Name of Work: 				LT ELECTRICAL WORK  –  AT IUCAA

A.	Name of Vendor  / Firm / Company		____________________________

____________________________

Postal Address					____________________________

____________________________

Telephone Nos.				____________________________

Telex / Fax					____________________________

Email ID					____________________________

Signature & seal of Bidder

| Technical Bid Form |
| --- |
| LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK at IUCAA Campus, Pune |
| Client : Inter University Center for Astronomy & Astrophysics, Pune |
| 1 | Company Name |  |
| 2 | Electrical Contractor's Licence No. and Validity Period/Date |  |
| 3 | Establishment Year |  |
| 4 | Address |  |
| 5 | Telephone Nos |  |
|  | Mobile no. |  |
|  | Fax Nos. |  |
|  | E-mail |  |
| 6 | Contact Person |  |
|  | Name |  |
|  | Designation |  |
|  | Mobile # |  |
| 7 | Organizational Capability (staff strength) | Name Qualification Experience |
| i | Project Managers |  |
| ii | Supervisors (PWD License Holder for LT & HT) |  |
| iii | Safety Engineers |  |
| iv | Quality Engineers |  |
| v | Technicians (PWD License Holder for LT Work) |  |
| 8 | Proposed Team for this Project |  |
| i | Project Managers |  |
| ii | Supervisors |  |
| iii | Safety Engineers |  |
| iv | Quantity Surveyors/Billing Engineer |  |
| v | Quality Engineers |  |
|  | (Provide similar details of all sub-contractors proposed to be used on project) |  |
| 9 | Financial Capacity over last 3 years (Turnover & Profit) |  |
|  | Financial year 2009-10 |  |
|  | Financial year 2010-11 |  |
|  | Financial year 2011-12 |  |
| 10 | Provide following details of Three major/best jobs (Costing Rs. 150 Lakhs & above) completed of similar nature in last Three Years (You may be required to arrange for inspections of at least two such projects). |  |
| a. | Name of the project |  |
|  | Consultant. |  |
|  | Completion year |  |
|  | Size |  |
|  | Value |  |
|  | Scope |  |
|  | Project proposed for inspection |  |
|  | Client contact details (Name with tele / fax and e-mail). |  |
| b. | Name of the project |  |
|  | Consultant. |  |
|  | Completion year |  |
|  | Work Size |  |
|  | Value |  |
|  | Scope |  |
|  | Project proposed for inspection |  |
|  | Client contact details (Name with tele / fax and e-mail). |  |
| c. | Name of the project |  |
|  | Consultant. |  |
|  | Completion year |  |
|  | Work Size |  |
|  | Value |  |
|  | Scope |  |
|  | Project proposed for inspection |  |
|  | Client contact details (Name with tele / fax and e-mail). |  |
| 11 | Work in hand (provide details in following format - Attach additional sheets if required) |  |
| 1 | Name of the project |  |
|  | Consultant |  |
|  | %age completed/status |  |
|  | Completion time |  |
|  | Size (sq.ft.) |  |
|  | Value. |  |
| 2 | Name of the project |  |
|  | Consultant |  |
|  | %age completed/status |  |
|  | Completion time |  |
|  | Size (sq.ft.) |  |
|  | Value. |  |
| 12 | Infrastructure/ Equipment/ Machinery details: |  |
| 13 | Insurance Cover. |  |
|  | Provide details of cover availed. |  |
| 14 | PF/ESI details :- |  |
|  | Reg. No. PF |  |
|  | Reg. No. ESI |  |
|  | Reg. No. WCT. |  |
|  | Reg. No. Service Tax |  |
|  | Reg. No. VAT |  |
|  | Reg No. CST |  |
|  | Reg No of Profession Tax Certificate |  |
| 15 | PAN Details: |  |
|  | PAN No: |  |
|  | Photocopy of PAN |  |
|  | Latest Income tax clearance certificate |  |
| 16 | Quality Assurance |  |
|  | Provide details of methodology adopted. |  |
| 17 | A brief enlistment of Architects/ Consultants with whom your organization has worked. |  |
| 18 | Major suppliers on previous projects |  |
| 19 | Major suppliers proposed for this project |  |
| 20 | Solvency certificate from Nationalised Bank of minimum Rs. 100 Lakhs |  |
|  | (Issued after January - 2012) |  |
| 21 | List any arbitration cases/ legal disputes on Current/ previous projects - Mention name of project, reason for dispute, party filing the suit and current status) |  |
| 22 | Is the company ISO Certified? |  |
| 23 | List any awards, recognitions on previously executed projects |  |
| 24 | Any other documentation relevant to Pre-qualification (Cnontractors can modify the tables to create additional space for information if required) |  |
| 25 | Prepared and Submitted by (Name & Signature) |  |
| Notes - 1) The Inter University Centre for Astronomy & Astrophysics, Pune reserves the right to accept or reject any or all applications without assigning any reasons. 2) Please support Work in hand and completed work information with copy of the work order from the client. |

INDEX

| SR. NO. | CONTENTS | PAGE NO. |
| --- | --- | --- |
| 01. | Cover Sheet | 0 |
| 02. | Index | 6 |
| 3.1 | Tender Notice Information | 3 - 4 |
| 3.2 | Instructions to Vendors | 5 - 8 |
| 04. | General Conditions of Contract | 9 - 42 |
| 05. | Technical Specifications | 43 - 89 |
| 06. | Bill of Quantities |  |
| 07. | List of Approved Makes | 90 - 91 |
| Appendix III | Proforma for Contract Agreement (Articles of Agreement) | 92 - 93 |

## Copy of News paper Advertisement

NOTICE INVITING TENDER

Sealed tenders are invited under two bid system (Technical and Commercial) for “LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK”. The vendors/contractors should have carried out at least three works of similar nature in last three years costing more than Rs 150 lakhs for reputed institutes.

The tender document and all details can be viewed and downloaded from the official web site of IUCAA ( http://www.iucaa.ernet.in/Tenders ) from  16/07/2012 to 18/07/2012. Demand draft of Rs.2000/- to be enclosed with Technical Bid as non refundable tender cost.

IUCAA reserves the right to reject any or all of the tenders without assigning any reasons.

TENDER  INFORMATION

Inter-University Centre for Astronomy and Astrophysics (IUCAA), Post Bag 4, Ganeshkhind, Pune 411 007, invites sealed tenders in “Technical & Financial Bid”  from eligible and qualified tenderers for “LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK”.

Date of sale of tender enquiry document	:  From 16/07/2012 to 18/07/2012   during							          	   	   11:30 hrs to 15:30 hrs.

Place of sale of tender enquiry documents	:  Cashier’s office, IUCAA

Submission of questionnaire for Pre-Bid	:  23/07/2012 up to 1700 hrs

Pre-Bid Meeting				:  24/07/2012 at 1500 hrs

Closing date & time for receipt of tender	:  09/08/2012 at 15:00 hrs.

Tender opening date & time			:  09/08/2012 at 15:30 hrs.

Place of tender opening			:  IUCAA’s office

Earnest Money Deposit			:  Rs.3,00,000/-  (Rs. Three Lakhs Only)

1.	Tender enquiry documents may be purchased on payment of a non-refundable fee of Rs. 2000/- (Rupees Two Thousand Only) per set in the form of cash or an account payee demand draft drawn on a Nationalised / Scheduled / Commercial Bank, in favour of  Inter-University Centre for Astronomy and Astrophysics (IUCAA) payable at Pune. Tender fees will be waived in case of firms registered under National Small Industries Corporation ( NSIC )

2.	Tenderers shall ensure that their tenders, complete in all respects, are dropped in the tender box located at the address given above on or before the closing date and time indicated as above, failing which the tenders will be treated as late and rejected.

3.	In the event of any of the above mentioned dates being declared as a holiday / closed day for IUCAA, the tenders will be sold/received/opened on the next working day at the appointed time.

4.	The tender enquiry documents are not transferable.

5.        IUCAA reserves the right to reject any or all of the tenders without assigning any reasons.

Administrative Officer (Purchase)

Inter-University Centre for

Astronomy and Astrophysics,

Post Bag 4, Ganeshkhind,

Pune 411 007

Tel. (020) 25604100 / 25691414

Fax (020) 25604699

SUBJECT : 	NOTICE INVITING TENDER (NIT) For “LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK AT IUCAA”

1. Owner : INTER-UNIVERSITY CENTRE FOR ASTRONOMY AND ASTROPHYSICS, PUNE

2. SITE ADDRESS :  Post Bag 4, Ganeshkhind, Pune University Campus, Pune - 411007

3. Description of work  : LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL  & HOSTEL BLOCK AT IUCAA,   PUNE

4.  Schedule of work  -    One month to coincide with the schedule and progress of other works counted from the date of LOI/WO

i) Important Note : Following BOQ Sr. Number's work completion period is 40 days only from date of LOI/WO  –

(A - 1.1, 1.2, 1.3, 1.4, 1.5, 1.6, 1.7, 1.8, 1.9)

(B - 1.1.1, 1.1.9, 1.2.0, 2.2.1, 2.2.8, 2.2.9, 3.1.2, 3.3.2)

(C - 1.1.1, 1.1.2, 2.2.2, 2.2.4, 4.4.1, 4.4.2)

ii) For remaining BOQ Sr. Number’s work completion period is 75 days to coincide with the schedule and progress of other works counted from the date of LOI/WO.

5. Form of Contract  -   Item Rate

6. Bid Documents  -  General Conditions of contract, Technical specifications, Drawings and the BOQ in hard copy is being issued with this  tender documents.

7. Receipt of Bids -  Bids should be submitted in sealed envelope marked as ‘TECHNICAL & COMMERCIAL BID’ for “LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK AT IUCAA, PUNE” will be received up to 1500 hrs on 09/08/2012 and same will be opened at 1530 hrs on 09/08/2012.

8. Earnest Money Deposit / Security Deposit :

EMD of Rs. 3,00,000/-  in the form of DD in favour of IUCAA from a nationalized bank should be submitted along with the Technical  bid. The successful bidder can opt to adjust the EMD amount towards payment of Security Deposit. SD will be 5% of the contract value. However, the balance amount of SD has to be deposited separately by DD. EMD will be waived in case of firms registered under National Small Industries Corporation ( NSIC )

9. Acceptance / Rejection of Tenders –

Tenders missing or with incorrect, inaccurate calculations or generally not complying with the conditions will be rejected. Tenderers  must return back all documents issued to them as part of Tender documents. Each document must be stamped and signed as token of acceptance. If the original documents are not returned, the bid shall be summarily rejected. The tenderer must fill the “vendor checklist for tender submission”, attached as part of Instructions to tenderers and submit it with the tender documents. Tenderers should quote their rates with the totals both in figures & in words. The total of each page along with carried over figures of the previous page shall be given in ink and signed by the tenderer. No blank space shall be left. No over writing or cutting will be accepted. In such cases the quote will be rejected without any other consideration. No alterations, amendments or modifications shall be made by the tenderer in the Notice Inviting Tenders, Instructions to the Contractors, Contract Form, Conditions of the Contract, Drawings and Specification and if any such alterations are made or any special conditions attached, the tender is liable to be rejected without reference to the tenderer. The acceptance of a tender shall rest with the Owner or its authorized representative who does not bind itself to accept the lowest tender and reserves to itself the right to reject any or all the tenders received without assigning any reason(s) whatsoever. Non acceptance of any tender shall not make the Owner liable for compensation or damages.

At any time prior to the Tender submission date, the Owner may, for any reason, whether on its own initiative or in response to a clarification requested by a tenderer amend the Tender documents by an Addendum (The “Addendum”) or issue Clarification memo.

The Addendum as well as clarification memo will be notified in writing to all Tenderers. Tenderers shall promptly acknowledge receipt thereof to the same person at the same address. Only amendments and clarifications to the Tender Documents made through Addendum or clarification memo will form part of the Tender Document.

10. If you have any questions /clarifications etc. it should be sent to administrative officer purchase on email (purchase@iucaa.ernet.in)

This notice inviting tender will form part of the tender document and the agreement executed by the successful tenderer.

Please note that there is an emphasis on completion of all works by the scheduled date of completion with strict adherence to quality and safety norms.

For further information or clarifications, the tenderer may contact the undersigned or IUCAA.

Kind regards,

Administrative Officer (Purchase)

Inter-University Centre for

Astronomy and Astrophysics,

Post Bag 4, Ganeshkhind,

Pune 411 007

Tel. (020) 25604100 / 25691414

Fax (020) 25604699

APPENDIX TO FORM OF TENDER

SUMMARY OF COMMERCIAL TERMS :

( Please refer Conditions of Contract for detailed explanation of Commercial Terms )

| Sr. No. | ITEM |  | DETAIL |
| --- | --- | --- | --- |
| 1 | Earnest Money |  | Rs. 3,00,000/- (Rupees Three Lakhs only) in the form of Nationalized / Scheduled Bank / Commercial Bank Demand Draft in favour of Inter University Centre For Astronomy and Astrophysics payable at Pune in separate sealed envelope. EMD will be waived in case of firms registered under National Small Industries Corporation ( NSIC ) |
| 2 | Mobilisation Advance |  | NIL |
| 3 | Security Deposit |  | 5 % of Contract Value by a Demand Draft within 10 days of issue of LOI / WO which will be converted into Retention Money. SD will be waived in case of firms registered under National Small Industries Corporation ( NSIC ) |
| 4 | Retention money against total works |  | Retention money will be 5% of the final bill amount. In case of short fall after adjusting Security Deposit, same will be recovered from interim and final bill. |
| 5 | Advance against Materials brought to site |  | IUCAA may pay only 5% secured advance against approved materials brought at site by contractor. |
| 9 | Time of Work Completion |  | For following BOQ Sr. Number's work completion period will be 40 days only from date of LOI/WO – (A - 1.1, 1.2, 1.3, 1.4, 1.5, 1.6, 1.7, 1.8, 1.9) (B - 1.1.1, 1.1.9, 1.2.0, 2.2.1, 2.2.8, 2.2.9, 3.1.2, 3.3.2) (C - 1.1.1, 1.1.2, 2.2.2, 2.2.4, 4.4.1, 4.4.2) ii) For remaining BOQ Sr. Number’s work completion period is 75 days to coincide with the schedule and progress of other works counted from the date of LOI/WO. |
| 10 | Compensation for Delay / Liquidated Damages |  | Half percent of Contract Price per week of Delay subject to a ceiling of 5% of final Contract Price. |
| 11 | Maintenance / Defect Liability Period for total Works |  | 14 Months from the date of Completion of all Works and acceptance by Owner or Manufacturer’s warranty period whichever is more. |
| 12 | Interim Bills Periodicity |  | Only two RA bills ( not less than Rs.30/- lacs ) |
| 13 | Time within which payment of Interim Running bill to be made after Project Manager’s Certification |  | Project Manager’s certification within 14 days of receiving the correct Interim invoice. Payment by Owner within 14 days of the issue of certificate for payment by the Project Manager. |
| 14 | Time within which payment of Final bill to be made after Project Manager’s Certification |  | Project Manager’s certification within 30 days of receiving the correct Interim invoice. Payment by Owner within 45 days of the issue of certificate for payment by the Project Manager. |
| 15 | Minimum Amount of Third Party Insurance (CAR Insurance Policy) |  | Bodily injury and Property damage not less than Rs. 1,00,000/- (Rs. One Lakh only) in each accident at each job site and not less than Rs. 5,00,000/- (Rs. Five Lakh only) for all accidents at all job sites as per prevailing Laws. |
| 16 | Workman’s Compensation Insurance |  | As per prevailing Laws Contractor must have policy against this law. |
| 17 | ESI, PF & other regulatory rules & laws. |  | Contractor to cover his workers & staff under ESI, & PF scheme and comply with local laws & statutes dealing with employment of persons Necessary reports to be submitted. |
| 18 | Workers accommodation |  | Contractor to make his own arrangements for accommodation of his workers & staff including site office, godown, storage yard, etc. outside site i.e. not with Owners premises. |
| 19 | All Inclusive Rates |  | Rates to be inclusive of all taxes & duties including. octroi, works contract/ turn over tax, etc. till the completion of work. |
| 20 | Venue of Arbitration and Arbitrator |  | Pune. Sole Arbitrator i.e. The Director, Inter University Centre For Astronomy and Astrophysics, Pune. |
| 21 | Jurisdiction of Courts |  | Pune. |

General Conditions of Contract

DEFINITIONS:

In the Contract (as herein after defined) the following words and expressions shall have meanings here by assigned to them, except where the context otherwise requires: (In alphabetical order)

  - Approved/Approval:  Approved/Approval shall mean approved/approval in writing

  - Approved Equal: Approved Equal shall mean an alternative product or service approved by the Project consultant being equivalent to that specified in the Contract Documents with prior approval of the Owner.

  - Construction Programme: ‘Construction Programme’ shall mean the programme to be furnished by the Contractor along with the Tender as prescribed in Notice Inviting Tender.

  - Contract: The Contract shall mean the agreement between the Owner and the Contractor for the proper execution and successful completion of the Work in accordance with the Contract Documents and further documents as may be expressly incorporated in the letter of intent/ acceptance.

  - Contractor: The Contractor shall mean the person or persons, firm, company or consortium whose tender has been accepted by the Owner and includes the Contractor's legal representatives, successors and persons assigned with prior approval of the Owner.

  - Contractor’s Representative:  The Contractor’s Representative shall mean the person or party duly appointed by the Contractor, act for and on its behalf on a day-to-day basis during the construction of the Work and the Project. Any action to be taken by the Contractor may be taken on the Contractor’s behalf by the Contractor’s Representative. The Contractor’s Representative shall be considered a “key person” for purposes of the General Terms of Contract. The Contractor shall provide an authority letter designating the Contractor’s Representative for the project.

  - Contract Documents: The Contract Documents shall collectively mean the documents to be listed in the Contract between the Owner and the Contractor and all modifications thereof and additions thereto incorporated in and made to any of those documents during the term of the Contract.

  - Contract Price:  Shall mean the total of price referred to in the Contract Documents for the Contractor’s performance of the Work. The prices mentioned in the order are firm and not subject to any escalation for any reason whatsoever unless specifically agreed by us. The charges for delivery at site and installation complete and the freight, insurance, loading, unloading, packaging and all other applicable charges involved in delivery of finished and installed product at site is included in the rates and the same shall be the responsibility of the Contractor. The total cost mentioned above shall cover cost of all equipment/ material, labour, wastage, transport of equipment/ materials to site, profit, custom clearance (if applicable), transit insurance (if applicable), installation, testing, commissioning and all incidentals complete. The bidder should quote their prices inclusive of all Taxes & levies. No extra claim for taxes will be entertained. The total cost is also inclusive of any shop drawings preparation (till the same are approved by consultants), engineering and site visits during the execution. The Contract is neither a fixed lump sum contract nor a piece work contract, but is an item rate contract to carry out the Work according to the actual measured quantities at the rates contained in the schedule of rates and probable quantities as provided in the Priced Bill of Quantities with Detailed Specifications. Item rates quoted in the bid proposal will be firm until the end of the contract. The Contract Price shall not exceed the amount as indicated in the Letter of Intent/Purchase Order. Amounts in excess of this number, not approved in advance by the Owner’s Representative shall be at the Contractor’s expense. The Contractor has to closely monitor the quantities and cost and obtain an Approval from the Owner/Project Consultant well in advance for any change outside the scope of the Work which would cause the cost of the Work to exceed the Contract Price as indicated in the Letter of Intent. No escalation in prices shall be allowed for any reason whatsoever during the period of the project.

  - Consultant: Shall mean any person or agency duly appointed by the Owner. Project consultants’ to act as ‘CONSULTANT’ to render consultancy services in any area/field of activity connected with and arising out of the Contract under a separate agreement setting out the consultant(s) responsibilities and terms.

  - Defect (S) Liability Period: Defect(s) Liability Period shall be 14 months after Virtual   Completion and any period extended as a result of rectification of the Work/change orders, between the Virtual Completion and the Final Completion of the Work, and during which period the Contractor shall be bound to replace and/or rectify and make good all defective materials, equipment and/or workmanship which arise in the Works or come to notice subsequent to the Virtual Completion of  the Works and prior to the Final Completion of the Works without requiring the Owner to bear any additional charges what so ever.

  - Drawings: ‘Drawings’ means all drawings, details and sketches along with the technical information therein, furnished by the Project consultant/ Consultant to the Contractor under the Contract and any modifications of such drawings or such other drawings as may be from time to time be furnished or approved in writing by IUCAA. All shop drawings, samples, patterns, models, operation and maintenance manuals, Product data and other technical information of a like nature submitted by the Contractor shall also be referred to as 'Drawings'.

  - Final Completion:  Final Completion will be deemed to have been achieved when at the end of the Defects Liability Period, all snags identified by the Project consultant have been remedied to the satisfaction of IUCAA, a Final Completion Certificate has been issued by the Project consultant when all the requirements of the Contract have been met and complied with and when all the defective items of Work and defects have been replaced and/or rectified and made good as directed by and to the satisfaction of the Owner.

  - Force Majeure:  Force Majeure are risks due to riots (other than those among Contractor's or its subcontractor’s/ supplier’s employees) and civil commotion (in so far as both these are uninsurable), war (whether declared or not), invasion, act of foreign enemies, hostilities, civil war, rebellion, act of terrorism insurrection, military or usurped power, an act of Government, an act of God, such as lightening, earth quake, unprecedented floods, tornado, and damage from aircraft etc.

  - Headings:  The headings in these General Conditions of Contract shall not be deemed to be part thereof or to be taken into consideration in the interpretation or construction thereof or of the Contract.

  - Letter of Intent : ‘Letter of Intent’ shall mean the document issued to the successful tenderer by the Owner signifying the Owner’s in-principle intent to enter into the Contract

  - Measurement Books: The “measurement books” shall mean the books maintained during the currency of the project to record all measurements qualifying for payment. The contractor shall maintain measurement books of all work done by them. The contractor shall get the measurement books verified by IUCAA authorities.

  - Nominated Sub Contractor: "Nominated Sub-Contractor" refers to those specialists, tradesmen and others, whose credentials as well as quotations are evaluated and approved by the Owner and then nominated for executing special works or supplying special equipment or materials, for which provisional sums are included in the Contracts. Such agencies shall be deemed to have been employed by the Contractor.

  - Owner: The Owner shall mean “IUCAA”, and the term Owner includes successors, assigns and affiliates.

  - Owner’s Representative: Owner’s Representative shall mean an employee/consultant of the Owner duly authorised to represent the Owner at site.

  - Project:  Project shall mean the total execution of the Work performed under this Contract for the “LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK AT IUCAA, PUNE”.

  - Public Holiday: ‘Public Holiday’ shall mean any day, which is declared as a public holiday by the Government of India or the State Government.

  - Project Coordination Services: ‘Project Coordination Services’ refers to those services, which need to be carried out by the Contractor in coordinating its work with the other agencies working at the Site as per instructions of the Owner / Project consultant. Such services shall be at no extra cost to the Owner and must be to the full satisfaction of IUCAA / Project consultant.

  - Project Consultant: The ‘Project Consultant’ mean any person /agency appointed by IUCAA as a project consultant. The Project consultant shall be authorized to represent and act on behalf of the Owner on a day-to-day basis during all stages of the Project. All communications, approvals and decisions to be taken in connection with the Project consultant’s services shall be channeled through IUCAA.

  - Provisional Sum: Provisional sum shall mean a lump sum included in the tender documents representing the estimated value of the Works for which details are not available at the time of issue of tender. For example: Housekeeping, provision of site office etc.

  - Records and Audits: ‘Records and Audits’ shall mean the books and records required to be maintained by the Contractor in such manner, so as to enable the Owner/ Project consultant  to carry out effective financial control.

  - Retention Money : ‘Retention Money’ shall have the same meaning ascribed to it in clause no.  27.3.

  - References and Cross-References To Clause And Sub-Clause Numbers : Unless specifically stated otherwise, all references and cross-references made to clause and sub-clause numbers in these General Conditions of Contract refer to the clauses and sub-clauses of the General Conditions of Contract itself.

  - Schedule of Rates : ‘Schedule of Rates’ shall refer to the rates forming the basis for the Contract Price, as provided in a schedule to the Contract.

  - Singular and Plural: Words in the singular also include the plural and vice versa where the context              requires.

  - Site: The Site shall mean the location “ IUCAA, PUNE CAMPUS”.

  - Specifications: "Specifications" means the technical specifications for the Work included in the Project consultant’s Drawings and the Electrical/Civil/MEP/ Other Works Technical Specifications, and any modification thereof or addition thereto.

  - Sub-Contractors: “Sub-Contractors” shall mean the persons, firms, companies or agencies who after approval of the Owner/ Owner’s Representative/ Project consultant , have entered into a direct Contract with the Contractor in respect of any part of the Work and any later package of the Project, and include the Sub-Contractors' legal representatives, successors and permitted assignee. The Contractor shall have full responsibility for the actions and work of any Sub-contractor whether contracted by the Contractor to perform portions of the Work or any later.

  - Tender: “Tender” shall mean the Contractor’s priced offer for execution and completion of Work and remedying any defects arising therein, in strict accordance with the Contract Documents as issued with the Tender and as per the agreement signed by the Contractor thereafter.

  - Tender Documents: “Tender Documents” shall mean the Contractor’s Proforma of Bank Guarantee for Performance Bond, the Proforma of Bank Guaranty against Mobilization Advance, , the proforma of Bank Guaranty against Retention Money and Notice Inviting Tender, General Conditions Of Contract, Special Conditions Of Contract, Works Technical Specifications, Bill Of Quantities With Detailed Specifications, Environmental, Health & Safety (EHS) Plan, Preliminary Project Construction Schedule, Drawing – Site Location, Drawings Of Project consultant & M&E Services Works and any other related documents.

  - Temporary Works: Temporary works mean all temporary works of every kind required for the execution of the Work by the Contractor.

  - Terms “and”, “or”, “and/or”: The terms “and, “or”, “and/or” used in context with the description or enumeration of two or more items or components of work of documentation or anything similar shall mean as is relevant and applicable to the text.

  - Tests on completion: Tests on completion shall mean all the system testing required to be done by the Contractor, to the entire satisfaction of Project Consultant, Owner and Owner’s representative, prior to Handing over the Site.

  - Vendors: “Vendors” shall mean and include all suppliers, contractors, sub-contractors, nominated sub-contractors engaged for the Project.

  - Virtual Completion: Virtual completion will be deemed to have been achieved upon a Virtual Completion Certificate being issued by the Project Consultant, when the Work, according to IUCAA and Project consultant, has been completed in every respect in conformity with the Contract Documents and are ready and fit for the intended purpose, complete with all systems and services having been tested and commissioned.

  - Written Notice: Written Notice shall be deemed to have been duly served if delivered in person to the authorized representative of the firm / company for whom it is intended, or if hand delivered at and a written delivery receipt obtained from such person or if sent through e-mail when confirmed through electronic mail (e-mail) as received by such person.. In case where written notice is sent by fax or courier service or speed post with acknowledgement to the last business address known to the party who gives the notice it shall be deemed to have duly served when it is actually served upon the other party.

  - Works: “Works” shall mean and include all materials, plant and machinery, equipment and labour necessary to execute the Project in full compliance with the requirements of the Contract Document.

  - Working day:  A working day is defined as any day between Monday and Saturday, both inclusive, and excluding any Public Holiday as notified by the Government of India/State Government.

2. SCOPE, EXTENT, INTENT AND OTHERS

  - Scope: The general character and the scope of the Work shall be as illustrated and defined in the  Drawings, Specifications, Schedule of Rates, BOQ and other Contract Documents.

2.2	Extent: The Contractor shall carry out and complete the Work under the Contract in every respect, and work shall include the supply of all labour, equipment, materials, plant and machinery, tools, transportation, form work, scaffolding and all things necessary for the proper execution and successful completion of the Work in accordance with the Contract Documents to the directions and satisfaction of IUCAA / Project consultant. The Contractor shall be fully responsible and liable for all matters in connection with or arising out of or being a result or consequence of its carrying out or omitting to carry out any part of the Work. Where any parts of the Work may be executed by or through Sub-Contractors, such responsibility and liability of the Contractor shall cover and extend to the work of all such Sub-Contractors.

2.3 	Intent: The Contract Documents shall be binding on the Contractor/ Contractor’s Representatives/ Sub-Contractors as the case may be. Wherever it is mentioned in the Contract Documents that the Contractor shall perform certain work or provide certain facilities and services, it is understood that the Contractor shall do so at its own cost. Materials or work described in the Contract Documents which have a well known technical or trade meaning, shall be held to refer to such recognised standards as are applicable to them.

2.4 	Instructions of  Estate  Manager: The Project consultant may from time to time, through the Estate Manager, issue further supplementary Drawings, written instructions, details, directions, and explanations, which shall be collectively referred to as the ‘Instructions of  IUCAA authorities. The Contractor shall forthwith comply with and duly execute the work comprised in such Instructions of IUCAA authorities, provided always that verbal instructions, directions and explanations given to the Contractor or Contractor’s Representative by the Project consultant or IUCAA authorities shall, if involving a variation, be confirmed in writing immediately thereafter by IUCAA.

2.5 	Approval of Estate Manager: Approval of the Estate Manager shall always mean approval in writing. The onus shall be on the Contractor to obtain all the necessary approvals in writing. Such approvals, however, shall not relieve the Contractor of any of its responsibilities under the Contract.

2.6 	Increases/Decreases to scope of Work: The Owner reserves the right to increase or decrease the scope of the Work on any or all items or to change the nature of the Work involved in any or all items or to completely delete any items of the Work under the Contract. The Contractor shall not be entitled to claim for loss of anticipated profits, for mobilization of additional resources, or for any other such reason on account of these change orders. In the event that the Owner elects in writing to add an item to scope of the project or to delete an item from its scope, the Owner shall be entitled to increase/ reduce (as the case may be) an appropriate amount from the Contract Price.

2.7  Items of work for completion:  The Contractor is bound to carry out any items of Work necessary for proper execution and completion of the Work even though such items of work may not be expressly be described in the Contract Documents.

2.8 Access for Owner, Project consultant :  The Owner, Owner’s Representative,  the Project consultant, and their respective consultants shall at all times have access to the Work and the Site and to the workshops or other places of the Contractor where the Work is to be so executed and in workshops or other places of Sub-Contractors and suppliers. The Contractor shall by a term in its Sub-Contracts so far as possible, secure a similar right of access to those workshops or places for the Owner, Owner’s Representative, Project consultant, and their respective consultants and shall do everything for the purposes of carrying out inspections to ascertain and ensure that Work is being carried out in conformity with the Contract Documents or for any other purpose in connection with the Work under the Contract.

3. PROJECT CONSULTANT / OWNER’S REPRESENTATIVE, CONTRACTOR & CONTRACTOR’S REPRESENTATIVE: The status, duties and responsibilities of the Project Consultant / Owner’s Representative, and Contractor/ Contractor’s Representative shall be as detailed below:

3.1 Role and responsibilities of the IUCAA Estate Manager / Department

i. The Estate Manager shall be responsible for the day-to-day supervision, progress monitoring, co-ordination and direction of the Project, and generally to ensure that the Work is carried out in all respects in strict conformity with the Contract Documents and timelines.

ii. The Estate Manager shall have the authority to stop the Work whenever such stoppage may be necessary to ensure the proper execution of the Project. The Contractor shall provide all the necessary facilities to the Estate Manager in the performance of his duties as a Estate Manager and shall comply with all instructions as may be issued by the Estate Manager. The Contractor shall refer all matters relating to the performance of the Contract to the Estate Manager. The Contractor shall not be entitled to claim extensions, extra costs or losses in this regard.

iii. The Estate Manager shall observe sound and established engineering practices using latest standards, codes and regulations, as applicable for the purpose specified and suitable for respective uses intended. Supervision over the Contractor shall be maintained by Estate Manager who shall exercise constant and continuous supervision and control over quality, workmanship and materials, plant, machinery, equipment etc. used for the Project as and when may be required.

iv. Estate Manager will work in close co-operation and co-ordination with the Project consultant for the execution of the Project in accordance with the Contract Documents.

v. All communication by the Contractor with the Owner or the Owner’s consultants shall be done through the Estate Manager.

3.2 Decisions: The Estate Manager in consultation with the Project consultant/ Consultant shall make decisions on all matters relating to the execution and progress of the Project, including the claims and queries of the Contractor. The decision, opinion, direction and interpretation of the Estate Manager (in consultation with Owner and/ or Project consultant/ Consultant), with respect to any or all matters including the following matters shall be final and binding on the Contractor, except for matters involving financial implications which shall be decided in consultation with and with the prior written approval of the Owner. Notwithstanding the generality of the foregoing, unless stated to the contrary below, the decision of the Estate Manager in respect of the following actions shall be binding upon the Contractor:

i. Any discrepancy in the Drawings and Specifications;

ii. The removal and/or re-execution of any work already executed by the Contractor.

iii. The dismissal from the Site of any person employed upon the Work by the Contractor or the Sub-Contractor.

iv. The opening up for inspection of any part of the Work covered up.

v.  All materials and workmanship used by the Contractor or the Sub-Contractors.

vi. Everything that must be provided or done by the Contractor in order to properly executes and successfully

completes the Work under the Contract.

vii. Delay and extension of time involved in the execution of the Works (only with prior approval of Owner).

viii. Supervising the replacing and/ or rectifying and making good all defective items of work and during the

Defects Liability Period.

ix. Removal of any material/equipment/plant and machinery brought by the Contractor to the Site for execution of

the Work.

3.3 Role and Responsibilities of the Contractor’s Representative:

i. The Contractor’s Representative shall represent the Contractor at the Site. The Contractor’s Representative shall be on Site at all times during performance of the Work and the Project Coordination Services and shall be responsible for the day-to-day interaction with the Estate Managers.

ii. The Contractor’s Representative shall have adequate experience in handling similar kind of projects, competent enough and have the authority to make and communicate all decisions called for in this Contract to be made by the Contractor. The Contractor’s representative may be required to produce appropriate documentation and referrals in respect of previous assignments. The Contractor’s Representative shall be responsible for the day-to-day supervision and oversight of the Project Coordination Services, including, without limitation, the EHS Plan implementation.

iii. The Contractor shall submit to IUCAA the name and other details of the Contractor’s Representative within 7 days of execution of contract.

3.4 Contractor’s Responsibilities: The Contractor shall have the following responsibilities in carrying out the Work and the Project Coordination Services.

i.The Contractor shall, on the instruction of the Estate Manager, immediately dismiss from the Work any person employed thereon by him who may, in the opinion of the Estate Manager, be incompetent or who engages in unlawful or disorderly conduct, and such persons shall not be re-employed on the Work without the prior written permission of the Estate Manager.

ii. Contractor shall indemnify the Owner for loss suffered by the Owner on account of any act/  omission/ neglect of the Contractor's workers, employees and Sub- contractors etc.

iii.The Contractor shall comply with all safety standards to the satisfaction of the Owner’s  representative/ Estate Manager.

iv. The Contractor shall take full responsibility for the management & supervision of the Sub-contractors and the Nominated Sub-Contractors and the Contractor’s Representative. The Contractor shall act as an independent contractor in the performance of its obligations under the Contract. The employees and the Sub-contractors utilised by the Contractor shall not be construed as the Owner’s employees and shall work under the control and management of the Contractor who shall be solely responsible for their acts & related risk. The Contractor shall be solely responsible for the payment of compensation and all statutory benefits of its employees and the employees shall be informed that they are not entitled to any of the Owner’s employee benefits. The Contractor and not the Owner shall be solely responsible for deduction and/or payment of all statutory payments including without limitation, provident fund, ESI,  MLWF,

workers’ compensation, disability benefits and unemployment  insurance or for withholding and paying

employment taxes viz. Profession tax and Income tax etc for the Employees. The employees and the    Subcontractors shall affirm they are not employees of the Owner for any  purpose and that they shall not exercise any rights, seek or be entitled to any benefit accruing to the regular employees of the Owner.

v. The Contractor shall ensure that all Sub-contractors engaged by it exercise such skill, care and technical competence to represent a high standard within their respective professions or trades as is appropriate for the satisfactory execution of their work and services.

vi. The Contractor shall exercise constant and continuous supervision and control over the workmanship,

materials, plant, machinery, equipment etc used in the Work and report on the status of the same to the Owner’s Representative and Estate Manager as and when required in terms of the Contract.

vii. The Contractor shall be responsible for obtaining all necessary permits, approvals, certificates and the like and submit the same to the IUCAA Estate Manager prior to the commencement of the Works.

viii. All the obligations and responsibilities of the Contractor under the Contract shall be duly fulfilled subject to the satisfaction of the Owner’s Representative and IUCAA Estate Manager.

ix. Any activity conducted or responsibility assumed by the Owner’s Representative or IUCAA Estate Manager shall not relieve the Contractor of any of its obligations and responsibilities under the Contract.

x. The Contractor shall observe sound and established engineering practices in the execution and completion of the Works in accordance with the Contract. The Contractor shall use latest standards, codes and regulations, as applicable for the purpose specified and suitable for respective uses intended. The Contractor must keep at site the latest IS codes for quick referencing.

4.0 SITE:

4.1 Contractor to satisfy itself about site conditions: The Contractor represents that before tendering for the Work, the Contractor has visited the Site and satisfied itself about the Site conditions for construction and for logistics and smooth flow of workmen and materials as well as permission from appropriate governmental authorities for this purpose. The Contractor has examined the Site and taken note of the correct dimensions of the Work, and facilities for obtaining any special articles called for in the Contract Documents. The Contractor has also made its own assessment and obtained all information on the Site constraints and on all matters that will affect the execution, continuation, progress, and completion of the Works. Any extra claims made in consequence of any misunderstanding, incorrect information on any of these points or on the grounds of insufficient description or information shall not be entertained or allowed at any stage

4.2 Access to site by the Contractor : The access to the Site will be given immediately on award of the Contract to the Contractor and the Site shall be shared with other Vendors as applicable. The Contractor shall upon being given such access commence the Work and diligently proceed with the execution of the Work in accordance with the Contract Documents. Access to the Site by the Contractor shall be merely a licence for carrying out the construction of the Work under the Contract, and the Contractor shall not by his being allowed such entry on the Site, acquire any right, lien or interest either in the Work carried out by them under the Contract or anything appurtenant or attached thereto or to any part of the Site, and its claim will only be in the nature of money found due and payable to them in accordance with the payment certificates under the provisions contained herein. The Work shall be free from all liens, charges and claims of whatsoever nature from any party other than the Owner. The Owner shall have a lien over all work performed by the Contractor, Sub-Contractor and Vendors and also for the materials and equipment brought on Site by them.

5. TYPE OF CONTRACT:  The Contract shall be an item rate Contract only to execute the Project according to the actual measured quantities, at the rates contained in the Schedule of Rates and probable quantities as provided in the Priced Bill of Quantities with detailed specifications. The Contractor shall be entitled to payment, in Indian Rupees, of no more than the Contract Price as stated in the Letter of Intent, in consideration of the Work performed and for the completion of the Work to the satisfaction of the Owner/ Owner’s Representative. The Contractor understands and agrees that the amount payable is assessed on a re-measurable basis in accordance with the tendered rates. However, the Contract Price may be altered on account of a change order issued in accordance with Clause 31 hereto. The Contract Price shall include payment for the supply of all labour (including payment to the Sub-Contractors), equipment, materials, plant and machinery, tools, transportation, framework, scaffolding, construction of civil works and shall also include all applicable taxes including the WCT, duties, octroi, levies, royalties, fees, insurance premiums, contributions towards employees benefits including ESI and PF and funds, provision and distribution of power and water and all services and activities constituting the Scope of Work defined in the General Conditions of Contract. The Contract Price shall also include the Contractor's establishment, infrastructure, overheads and all other charges, and shall generally be inclusive of every cost and expense required by the Contract to be borne by the Contractor and necessary for the proper execution and successful completion of the Work under the Contract in conformity with the Contract Documents and the best engineering and construction practices and to the satisfaction of the Project consultant, IUCAA Estate Manager. No escalation of the prices shall be allowed during the period of the Contract for any reasons whatsoever and the prices quoted by the Contractor shall be deemed to be fixed and constant throughout the duration of the Project and Defects Liability Period.

6. TAXES, DUTIES ETC.:  The total cost mentioned above shall cover cost of all equipment/ material, labor, wastage, transport of equipment/ materials to site, profit, transit insurance (if applicable), installation, testing, commissioning and all incidentals complete, inclusive of all Taxes and duties. However, any statutory variation shall be absorbed by you without any impact being passed onto the clients. The total cost is also inclusive of any shop drawings preparation (till the same are approved by consultants), engineering and site visits during the execution.

7. NOTICES, FEES, BYE-LAWS, REGULATIONS, ETC. : The Contractor shall comply with all applicable laws and government acts including the by-laws or regulations of local authorities relating to the Work in so far as construction, fabrication and installation activities are concerned, and it shall obtain from the local authorities all permissions and approvals required for the plying of trucks, construction of machinery etc., and also for construction of temporary offices, labour camps, stores and other temporary structures in connection with the Work, and the Contractor shall give all notices and pay all fees and charges that are and that can be demanded by law there under. In the Contract Price for the Work, the Contractor shall allow for such compliance and work, and for the giving of all such notices, and shall include the payment of all such fees and charges. However, no title or proprietary interest of any kind shall be created in favour of the Contractor by virtue of erection of the temporary structures.

8. LICENCES AND PERMITS:  The Contractor shall directly obtain all licences and permits for the materials under Government control, and those required to be obtained by the Contractor for the execution of the Work. The Contract Price shall include all transportation charges and the other expenses that may be incurred in this connection.

9. ROYALTIES AND PATENT RIGHTS: All royalties or other sums payable by the Contractor in respect of the supply and use of any patented articles, processes or inventions for the carrying out of the Work as described by or referred to in the Contract Documents, shall be deemed to have been included in the Contract Price. The Contractor shall keep the Owner indemnified against all such demands as may arise on account of payment of royalties.

10. INSURANCE: Before commencing the execution of the Work, the Contractor, without limiting his obligations and responsibilities under this Contract shall insure in the joint names of the Contractor and Owner, against his liability for any material or physical damage, loss or injury which may occur to any property, including that of the Owner/ IUCAA Estate Manager / Project consultants, Sub-Contractors, Vendors or to any person including any employee of the Owner/ Estate Manager / Project consultant, Sub-Contractors, Vendors or a member of the general public, by or arising out of the execution of the Work or in carrying out the Contract. The contractor shall ensure that the Owner and Project Manager are named as an additional beneficiary in all such insurances obtained. The contractor shall provide a copy of such policy on or before the date of execution of the Contract. The Contractor shall insure against all such liabilities and shall continue such insurance during the currency of the Contract including the Defects Liability Period. Premium for all insurance policies shall be paid and borne by the Contractor and shall not be reimbursable. The Contractor shall produce to IUCAA Estate Manager all certificates of insurance with in 7 (seven) days from the date of letter of intent/award. These certificates shall be fully executed and shall state that the policies cannot be cancelled until completion of the Contract. The Contractor shall obtain written confirmation of similar certificates from all Sub-Contractors and thereby assume responsibility for any claims or losses to the Owner resulting from failure of any of the Sub-Contractors to obtain adequate insurance protection in connection with their work and shall indemnify the Owner accordingly. It shall be obligatory for the Contractor to obtain and retain for all relevant times the insurance cover (in the joint names of the Contractor and Owner) under the following policies:

10.1 Contractor's All Risk Insurance Policy to inter alia cover the following:

i. The entire contract value (including the Contract Price plus 10% of the Contract Price for the period of completion of the Works or any extended period.

ii. Civil commotion, riots, war and other disturbances

iii.All Plant and machinery owned by the Contractor for the project.

iv. Damage insurance against loss or damage by fire or any other disaster to the works.

10.2 Third Party Insurance Policy : The contractor shall take a Third party insurance to cover for any damages to third party. This policy shall be effective up to the end of the Project including any extensions granted and shall include any damage to the properties including surrounding and adjacent properties and/or injury including death to the persons of the general public and anyone else deemed to be third party subject to individual claims not exceeding Rs.2,00,000/-limited to a maximum sum of Rs.10 Lakhs.

10.3 Workman’s Compensation Policy :  Policy to cover Contractor's liability under Workmen's Compensation Act 1923, Minimum Wages Act 1948, Contract Labour (Regulation and Abolition) Act 1970 and other relevant Acts listed elsewhere to cover the Contractors liability under the applicable labour laws. This shall be for the period up to Final Completion of the Work. The Contractor’s liability under this policy shall also include the Sub-contractors liability under the applicable labour laws.

10.4 Failure to insure:  If the Contractor fails to comply with the terms of this clause, the Owner may effect the insurance and deduct the expenses from any moneys that may be or become payable to the Contractor or may, at his option, refuse payment of any monies to the Contractor until the Contractor complies with this condition.

10.5 No limit to liability:  In addition to the liability imposed by law upon the Contractor for injury (including death) to persons or damage to property by reason of the negligence of the Contractor or his agents, which liability is not impaired or otherwise affected hereby, the Contractor hereby assumes liability for and agrees to hold the Owner harmless and indemnifies him from every expense, liability, payment, claim by reason of any injury (including death) to persons or damage to property suffered on account of any act or omission on the part of the Contractor, his employees, agents, servants, workmen, suppliers assigns or any of his Sub-Contractors, or any person directly or indirectly employed by any of them or from the conditions of the Site or any part of the Site which under the control of the Contractor or its employees or any of its Sub-Contractors, or any one directly or indirectly employed by either of them or arising in any way from the Work.

11 CONTRACTOR’S SITE ORGANIZATION, INFRASTRUCTURE AND RESOURCES :

11.1 Contractor’s representative and supervisory staff :

i. The Contractor shall at its cost provide and ensure continued effective supervision of the Work with the help of the Contractor’s Representative, assisted by full time qualified, experienced and competent engineers, supervisors, Safety officers, Safety stewards and adequate staff, to the satisfaction of the Owner’s Representative and the IUCAA Estate Manager for the entire duration of the Work.

ii. The Contractor shall submit its proposed site organization chart for the approval of the IUCAA Estate Manager.

iii. The Contractor’s Representative shall be on the Site at all times as the Work and the Project progresses and shall be responsible for carrying out the Work to the true meaning of the Drawings, Specifications, Conditions of Contract, Schedule of Rates, the other Contract Documents, and instructions and directions of the Owner’s Representative and the IUCAA Estate Manager.

iv. The instructions and directions given in writing to the Contractor’s Representative or to any of its assistants at the Site by the Owner’s Representative or the IUCAA Estate Manager shall be deemed to given to the Contractor officially. Attention is called to the importance of the Contractor requesting written instruction from the Owner’s Representative or the IUCAA Estate Manager before undertaking any Work where the IUCAA Estate Manager's and/or Owner’s Representative direction or instructions

are required. Any such Work done in advance of such instructions will be liable to be removed at the Contractor's expense and will not be paid for unless specifically approved in writing by the IUCAA Estate Manager and/or Owner’s Representative, as the case may be. It shall be the Contractor’s responsibility to provide written intimation to Owner’s Representative or the IUCAA Estate Manager, well in advance, all through the execution of the Project, if the work is likely to get disrupted or delayed due to non-issuance of drawings/ instructions.

v. All key staff employed at the Site by the Contractor shall be considered essential to the performance of the Work and the Project Coordination Services, and all key staff shall be subject to the approval of the Owner’s Representative. However such approval shall not relieve the Contractor of any of its contractual obligations with respect to the staff employed by the Contractor. No staff including the resident engineer and other technical supervisory staff shall be removed or transferred from the Work without the prior written permission of the Owner’s Representative or IUCAA Estate Manager.

vi. The Owner’s Representative and IUCAA Estate Manager shall, however, have the authority to order the removal from Site of any undesirable personnel from Contractor’s side due to their misconduct, incompetence or negligence in the performance of their duties. If key staff becomes unavailable for

performing the Work or the Project Coordination Services for reasons beyond the Contractor’s control, the Contractor shall immediately notify the Owner’s Representative to evaluate the impact of the same on the project. Prior to substitution or addition of any key staff, the Contractor shall obtain the Owner’s Representative’s written consent as to the acceptability of replacement or additions to such personnel.

vii. The Contractor shall at all times be solely responsible for the acts, omissions, defaults and neglect of all of its representatives, agents, servants, workmen and suppliers and those of its Sub-Contractors.

11.2 Man-power, plant and machinery:

i. The Contractor shall at its own cost provide and install all equipment, materials, plant, cranes, hoists, ladders, and scaffolding, necessary for the execution of the Work in conformity with the Contract Documents to the satisfaction of the Owner’s Representative and IUCAA Estate Manager. All machines, tools, trucks, formwork material, man-power and every thing else necessary for the proper and satisfactory execution and completion of the Work in accordance with the Contract Documents shall be provided by the Contractor at its own cost.

ii. The Contractor shall within one week of the award of Contract submit a complete list of its manpower, plant and machinery for the approval of the Owner’s Representative and IUCAA Estate Manager, which approval however, shall not relieve the Contractor of any of its responsibilities, obligations and liabilities under the Contract. The Contractor shall augment its manpower, plant and machinery without extra cost to the Owner whenever required or so directed by the Owner’s Representative/IUCAA Estate Manager in order to conform to the approved construction programme for the achievement of milestones and Virtual Completion of the Work.

iii. All the tools, equipment and machinery provided by Contractor for the execution of the Project should be in perfect condition. Any fault or non-operation of the tools, equipment and machinery, shall be rectified immediately by the Contractor and no time extension to the approved construction programme shall be allowed at all in the event of some fault of non-operation of tools, equipment and machinery.

11.3 Security: The Contractor shall at its own cost provide at all times adequate number of watchmen/ security personnel to guard the Site, the materials and equipment, to the satisfaction of the Owner’s Representative/ IUCAA Estate Manager. The Contractor shall at all times be fully responsible for the security of all materials and equipment on the Site, whether it’s own or those of any Sub-Contractor. Neither the Owner nor the Owner’s representative / IUCAA Estate Manager shall be responsible for any loss due to theft, fire, accident or any other reasons, whatsoever. Additionally, the Contractor shall, within seven days of the execution of the Contract, provide all necessary details of the security agency providing the watchmen/ security personnel for obtaining the written approval of the IUCAA Estate Manager.

11.4  Water and electricity: Tap off’s for temporary water and electricity shall be provided on site at single source ( free of cost ).  The Contractor shall make its own arrangement thereafter from the Tap off’s for Works and all costs in relation thereto shall be borne solely by the Contractor.

11.5  Scaffolding, Staging, Guard Rails, Barricades:  The Contractor shall at its cost provide steel scaffolding, staging, guard rails, barricades and safety barriers around all openings and at all edges, temporary stairs and other temporary measures required during the Project. The supports for the scaffolding, staging guard rails, barricades and safety barriers and temporary stairs shall be strong and adequate for the particular situations, tied together with horizontal pieces and braced properly. The temporary access to the various parts of the building under construction shall be rigid and strong enough to avoid any chance of mishaps. The entire scaffolding arrangement together with the staging, guard rails, barricades and safety barriers, and temporary stairs shall be to the approval of the IUCAA Estate Manager which approval shall not relieve the Contractor of any of its responsibilities, obligations and liabilities in relation to the safety requirements and for timely completion of the Work in accordance with the approved construction schedule. The use of wooden scaffolding on the Site is strictly forbidden.

11.6 Safety Equipment: The Contractor shall provide all the personal protective equipments like safety helmets, safety boots/shoes, protective clothing, etc., at its own cost to the Owner’s, Owner’s Representatives, IUCAA Estate Manager’s, Project consultant’s & their team within three days from the execution of the Letter of Intent of the Tender

11.7 Protection of Environment: The Contractor understands that the Site must be free from pollutants at the time of access to the Site and commencement of the Work. The Contractor shall comply with all applicable environmental laws and regulations and shall ensure that the Site is and remains free from pollutants till the end of the Project. The Contractor shall ensure inter alia, that neither the soil nor the ground water is polluted or contaminated by fuels or lubricants emitted by machinery operated on the Site or by other dangerous or poisonous substances which are or are deemed to be hazardous to the environment. Notwithstanding the above, the Contractor shall comply with all the directions and decisions of the IUCAA Estate Manager in this regard and all applicable environmental legislations in relation to the same including obtaining statutory consents and approvals as may be required.

Contractor thereof.

The Contractor shall ensure that all operations by the Contractor, its workmen, employees, Sub-Contractors to complete the Project and the remedying of any defects therein shall, so far as compliance with the requirements of this Agreement permit, be carried on so as not to interfere unnecessarily or improperly with:

a)  the convenience of the public, or

b) the access to, use and occupation of public or private roads, railways and footpaths to or of properties whether in the possession of Owner or of any other person.

c) the Owner’s operation and utilization of the facility at the Site; and

d) the Work of Vendors. If any hazardous or obnoxious materials (as defined by Indian law) are specified for use or are being used by Vendors, the Contractor shall keep record of such material and forthwith give written notice to the Owner and shall ensure that the Sub-Contractors and Vendors, as applicable, use, store and dispose of such hazardous or obnoxious materials strictly in accordance with all applicable laws.

12.0 Additional Safety Regulations: The Contractor shall continuously maintain adequate protection for the Work against fire and other hazards and shall protect the Owner’s property and the Site from damage or loss during the performance of this Contract. The Contractor also shall adequately protect property adjacent to the Site.

The Contractor shall take all necessary precautions for the safety of its employees, Subcontractors and the Vendors performing the Work and shall comply with all applicable safety laws and regulations to prevent accidents or injury to persons on, about, or adjacent to the Site. The Contractor shall be responsible for co-ordinating a safe working programme with the Owner’s Representative and the IUCAA Estate Manager. Such a programme shall include, and the Contractor shall be responsible for maintaining, the following safe working conditions and practices:

i. All combustible material, food matter, garbage, scrap, and other debris generated during the performance of the Work shall be collected and removed from the Site daily. Arrangements for scrap burning should be discussed with Owner’s representative.

ii. An adequate number and type of fire extinguishers shall be provided at the Site for fire control and shall be kept/maintained in satisfactory and effective working condition, at all times.

12.1 Requirement of Fire Extinguishers  Each gas welding or burning, arc welding unit, tar pot, or open flame unit requires a fire extinguisher with it during operation.

12.2 Requirement of Equipment : The availability of fire blankets is recommended at the Site. Other equipment related conditions are as follows:

i.   The Contractor shall use all equipment, which is in good condition. The Contractor shall not use or permit to be used the Owner's equipment and the Owner shall not use the Contractor's equipment without prior written permission of the other.

ii.  When working in an occupied building or area, the Contractor must before commencement of work familiarise itself with the hazards of that area, such as the location of flammable substances and toxic fumes.

iii.  Materials and equipment intended for installation in the Work as well as the Owner's equipment and materials already in place are to be protected at all times from debris, weather, or any damage. The Contractor shall take all steps necessary to ensure the preservation condition of such equipment.

iv.  The Contractor's materials, tools, and equipment shall be stored only in areas approved by the Owner for this purpose.

v. Site access and parking by the Contractor's personnel shall be at locations designated by the Owner/ IUCAA Estate Manager. Only the Contractor's personnel necessary for the performance of the Work shall be permitted access to the Site. The Contractor and its employees and Sub-contractors shall adhere to all speed limits and traffic regulations at the Site.

vi. The Contractor and its employees and subcontractors shall strictly obey all "No Smoking" restrictions.

vii. The Contractor shall not operate or use or manipulate utilities at the Site without the Owner's prior written approval.

viii. No valves shall be turned off or on, or electrical disconnect switches operated except in an emergency. Any required utility "shut downs" will be scheduled and co-ordinated by the Owner’s Representative.

ix. The Contractor shall make any requests for utility manipulation or "shut downs" in writing to the IUCAA Estate Manager at least five days advance notice.

12.3. Safety with regard to site and housekeeping:

i. The use of intoxicants or unlawful drugs at the Site, in any degree, shall be strictly prohibited. The Contractor shall rigorously enforce this regulation.

ii. When overhead work is in progress in or around an occupied area, signs to denote such work prominently displaying “Overhead Work” shall be used or the area shall be protected by barricade.

iii. Dusty work, such as concrete breaking or demolition, in or near occupied areas, shall proceed only after wetting down the area and taking steps necessary to prevent dust from penetrating occupied areas and creating a nuisance.

iv. Care shall be taken not to block any door, passageway, safety exit, fire fighting equipment, or safety equipment with materials or equipment.

v.  Contractor shall maintain general cleanliness at site. All waste and debris shall be stored at designated place and disposed regularly. Site should be cleaned as per instruction given by Estate Manager at the end of day.

vi.  Materials must be piled, stacked, or stored in a neat and orderly manner.  All stacking, whether inside or outside a building, shall be parallel to or at right angles to the building line or fence.

vii.  When noisy operations of a prolonged nature are necessary in or near an occupied area, arrangements must be made with the Owner’s Representative for scheduling to minimize any nuisance in the occupied area.

12.4 Non-compliance of Regulations : If the IUCAA Estate Manager or the Owner’s Representative notifies the Contractor  of non-compliance with the foregoing regulations, the Contractor shall immediately, if so directed, or in any event not more than Twenty four (24) hours after receipt of such notice, make all reasonable efforts to correct/ rectify such non-compliance. If the Contractor fails to do so, the Owner may suspend all or any part of the Work. The, Owner shall lift the suspension of the Work only upon the satisfactory corrective action undertaken by the Contractor in this regard. The Contractor shall not claim any extension of time to complete the Work or additional fees due to any such work suspension.

12.5 Implementation of Safety Measures Notwithstanding anything herein before contained, particularly in clause 12.5,

12.6  the Contractor shall be liable to ensure and implement all safety measures, whether or not statutorily prescribed, to safeguard, preserve and protect the life, health and welfare of every workman employed/deployed/engaged directly or indirectly by the Contractor on the Site and in relation to or connected with the Work and all Vendors employed in later phases of the Project in addition to installing, providing every prescribed safety and protective equipment, clothing etc., and the mere absence of any reference to or specification of a particular statute or rule or regulation in this Contract shall not absolve the Contractor of an obligation to comply with every such law, rule or regulation. The Contractor shall be liable for all consequences/liabilities arising out of its violating any of the aforesaid provisions, including fines, penalties, compensations, damages, prosecutions, proceedings, medical expenditure and costs, rehabilitation costs and all other expenses connected therewith.

13 CONTRIBUTION TOWARDS EMPLOYEE BENEFITS, FUNDS ETC.: The Contractor shall include in the Contract Price all expenses necessary to  meet its obligations for making contributions toward employee benefits funds (Such as provident fund, ESI benefits, old age pension and/or any other benefits/compensation legally payable) in compliance with all the statutory regulations and requirements. All records in this connection shall be properly maintained by the Contractor and produced for scrutiny by the concerned authorities, IUCAA Estate Manager and the Owner whenever called for.

14 SETTING OUT AND SITE SURVEYS: The Contractor shall establish, maintain and assume responsibility for all bench marks and grid lines, and all other levels, lines, dimensions and grades that are necessary for the execution of the Work, in conformity with the Contract Documents. The Contractor shall establish its relation to the permanent benchmarks and boundary lines established at the Site. The Contractor shall verify and co-relate all the survey data available at the Site before commencing the Work and shall immediately report in writing any errors or inconsistencies to the IUCAA Estate Manager. Commencement of Work by the Contractor shall be regarded as its acceptance of the correctness of all survey and setting out data available at the Site and no claims shall be entertained or allowed in respect of any errors or discrepancies found at a later date. If at any time error in this regard appears during its progress of the Work, the Contractor shall at its own expense rectify such error to the satisfaction of the IUCAA Estate Manager/ Owner. The approval by the IUCAA Estate Manager of the setting out by the Contractor shall not relieve the Contractor of any of the responsibilities, obligations, and liabilities under the Contract.

The Contractor shall be entirely and exclusively responsible for the horizontal, vertical and other alignment for all levels and dimensions and for the correctness of every part of the Work, and he shall rectify effectively any errors or imperfections therein. All such rectifications shall be carried out by the Contractor at its own cost and to the instructions and satisfaction of the IUCAA Estate Manager. The Contractor shall employ qualified surveyors to carry out all the surveys and setting out works in this regard.

15 DRAWINGS, SPECIFICATIONS, INTERPRETATIONS ETC.:  Within 10 days from the issue of Letter of Intent/ Purchase/Work Order, the Contractor shall be furnished by the IUCAA Estate Manager and/or Owner’s Representative with one copy each of the Conditions of Contract, Specifications, and Schedule of Rates, without cost to Contractor for its own use and for the use of its Sub-Contractors until the completion of the Contract. Additional copies of Contract Documents will be supplied on payment at actual cost basis. Three copies of the working drawings shall be provided by the Project consultant through IUCAA Estate Manager to the Contractor as the Work progresses. The time and the date for the provision of the Drawings shall be mutually agreed between the Contractor and Owner’s Representative / IUCAA Estate Manager / Project consultant in conformity with the construction programme and with due regard for the need to order and specify materials and equipment to the Site.

In general, the Drawings shall indicate the dimensions, positions and type of construction, the Specifications shall stipulate the quality and the methods and performance criteria, and the Schedule of Rates shall indicate the rates for each item of work for evaluating change orders. However, the above Contract Documents being complementary, what is called for by any one shall be binding as if called for by all. Matters not contained in the Specifications and in case of any ambiguities in the written Specifications of the Contract, the Works shall be executed as per relevant BIS codes and CPWD Specifications in that order of preference. If such codes have not been framed, the decision of the Project consultant in the matter shall be final and binding on the Contractor. Any Work indicated in the Drawings and not mentioned in the Specifications or vice versa, shall be deemed as though fully set forth in the Drawings or Specifications as the case may be. Work not specifically detailed, called for, marked or specified, shall be the same as similar parts that are detailed, marked or specified. From time to time during the progress of the Work, the Contractor will be issued with revisions of Drawings and written instructions by the IUCAA Estate Manager in connection with and necessary for the proper execution and successful completion of the Work. All such revisions of Drawings and written instructions shall be part of the Contract Documents and the Contractor shall be bound to carry out the work that is shown and detailed on all such Drawings and shall be bound to follow and comply with all such  Instructions. All Drawings and their subsequent revisions will be issued to the Contractor by listing such Drawings on the transmittals by the Project Manager. The Contractor shall maintain a Drawing register listing all Drawings and their latest revisions. All superseded Drawings shall be so stamped and withdrawn from circulation at the Site. It shall be the responsibility of the Contractor to ascertain and ensure that all the Work is carried out in accordance with the latest revisions of the Drawings issued to him. Should the Contractor fail to do so, all the rectifications and remedial work that may be required to conform to the latest revisions of the Drawings shall be at the Contractor's sole expenses.

Wherever it is mentioned in the Conditions of Contract, Specifications, and other Contract Documents that the Contractor shall perform certain work or provide certain facilities, it is understood that the Contractor shall do so at its own cost, unless otherwise provided in the said Documents.

The Contractor shall immediately in writing bring any errors or inconsistencies in the Drawings and Specifications to the attention of the IUCAA Estate Manager for interpretation or correction before proceeding with the affected portion of the Work, and no claims or losses alleged to have been caused by such discrepancies shall be entertained or allowed at any stage. Local conditions, which may affect the Work, shall likewise be brought to IUCAA Estate Manager attention at once. If at any time it is discovered that work, which has been done or is being done is not in accordance with the approved Drawings and Specifications, the Contractor shall correct the work immediately. Correction of such work shall be at the expense of the Contractor and shall not form a basis for any claims for payment or extension of time. The Contractor shall carry out all the rectification work only after obtaining the approval for the same from IUCAA.

The Contractor, in the execution of the Work, shall make no deviations from the Drawings, Specifications, and other Contract Documents. Interpretations and clarifications shall be issued by the Project Consultant / IUCAA, which shall be binding on the Contractor.

No scaling of any Drawing shall be done to obtain the dimensions. Figured dimensions on the Drawings shall be used for carrying out the Work. Drawings with large-scale details shall take precedence over small scale Drawings. Where any Drawings and details have not been provided but are necessary for the execution of the Work, it shall be the responsibility of the Contractor to seek these drawings and details in writing from IUCAA Estate Manager at least four weeks prior to the latest date by which the Contractor needs these drawings and details to suit the programmed execution of the Work. No extension of time shall be allowed for any delays caused due to the Contractor's failure to seek such details.

Drawings, Schedule of Rates, Specifications, and other Contract Documents, and all copies thereof furnished by the Project Manager shall be treated the Owner's property at all times. Such Drawings, Schedule of Rates, Specifications, and other Contract Documents shall not be used on any other work and shall be returned to the Owner at its request or at the completion of the Work in accordance with the Contract. In case of any discrepancy in the interpretation of drawings, the decision of IUCAA shall be binding.

16 ASSIGNMENT AND SUBLETTING : The Contractor shall not assign this Contract or any part of it. The Contractor may, however, sub-contract any part of the Work with the prior written consent of IUCAA. The Owner/ Owner’s representative/ Project consultant/ Estate Manager  reserves the right to review and approve each Sub-contractor which the Contractor recommends at any time to engage to perform any services before such Sub-contractor is hired or performs any service. Any permission to sub-contract any parts of the Work shall not relieve the Contractor from any of its responsibilities, obligations, and liabilities under this Contract.

17 NOMINATED SUB-CONTRACTORS: As soon as practicable, but at least one week before awarding any sub-contract, the Contractor shall submit to the Project consultant, IUCAA Estate Manager and the Owner’s Representative in writing the names of the Nominated Sub-Contractors proposed for any part of the Work, for the approval of the same by the Project consultant / IUCAA . The Contractor shall employ such Sub-Contractors only after he has received confirmation in writing of such approval from Estate Manager and the Owner’s Representative. Such approval, however, shall not relieve the Contractor of any of its responsibilities, obligations and liabilities under the Contract. The Contractor shall be responsible for the acts, defaults, omissions and neglect of all Sub-Contractors and their agents, servants and workmen. The Contractor shall not employ any Sub-Contractor to whom Estate Manager or the Owner’s Representative object and/or does not approve. The Project consultant may by written instruction inform the Contractor, waiving the need for the Project consultant to specifically approve the Sub-Contractors in addition to the approval of IUCAA.

18 SEPARATE CONTRACTS: The Owner reserves the right to enter into separate other contracts in connection with the Project. The Contractor shall afford other contractors reasonable opportunity for their access to the Site, for the storage of their materials, and for the execution of their work, or if specified give assistance to such contractors for such purposes as are specified. The Contractor shall properly connect and co-ordinate its Work with that of the other contractors that may be employed or engaged by the Owner. If any part of the Contractor's Work depends for its proper execution or results upon the work of any other contractor, the Contractor shall inspect and promptly report in writing to IUCAA, any defects in such work that render it unsuitable for such proper execution and results. The Contractor's failure to inspect and report such defects shall constitute as an acceptance of the other contractor's work as fit and proper for receiving the work of the Contractor.

19 CO-ORDINATION OF WORK : At the commencement of the Work, and from time to time, the Contractor shall cooperate with other contractors, Sub-Contractors, persons engaged on separate contracts in connection with the Project, Vendors and the Project consultant and with the Owner’s Representative for the purpose of the co-ordination and execution of various phases of the Project. The Contractor shall determine and ascertain from the Vendors and persons engaged on separate contracts, in connection with the Project, the extent of all chasings, cutting and forming of all openings, holes, details of all inserts, sleeves, etc. that are required to accommodate the various services.

The Contractor shall determine and ascertain the routes of all services and positions of all floor and wall openings, outlets, traps, the details of all inserts, equipment and services and shall carry out the construction and making good of all "builder's work" in accordance with and as shown, described and/or measured in the Drawings, Specifications, and other Contract Documents. Also, the Contractor shall ensure that all required services, inserts, sleeves, embedment etc. are in place/position before he proceeds with its work. Should the Contractor fail to comply with these requirements and the consequence of such failure necessitates the breaking, re-doing and making good of any work, then the cost of all such breaking, re-doing and making good of any work shall be to the account of the Contractor and shall be borne by him. No breaking and cutting of completed work shall be done unless specifically authorised in writing by IUCAA Estate Manager. No work shall be done over broken or patched work without first ascertaining that the broken surface is adequately prepared and reinforced to receive and hold further work, as determined by Estate Manager. In order to ensure proper co-ordination is being undertaken, weekly meetings, chaired by SAO / IUCAA authorities will be held with the various contractors and at which coordination will be discussed and minutes of actions proposed circulated.

20 WORK ON NON WORKING DAYS:  If it is necessary for the Contractor or any Sub-Contractor to work on days other than Working Days or outside the normal working hours in order to keep up to the time schedule and meet the Construction Programme, the Contractor shall obtain the prior approval of IUCAA in writing. Even if any work is carried out at site on a non Working day with prior written permission of IUCAA, the Contractor shall be solely responsible for extra cost including but not limited to wages. Applicability of all other terms and conditions of contract on such days would be same as applicable for a Working day.

21 MATERIALS, WORKMANSHIP, STORAGE, INSPECTIONS ETC.:

21.1 Materials and workmanship: The Contractor shall be responsible for the establishment of a full and comprehensive quality control system for the Work. The system shall include, but not be limited to, the means of controlling the testing and receipt of materials, the inspection of the Work, the filing and ordering of Drawings and correspondence and the duties and responsibilities of staff members.

All materials and equipment to be incorporated in the Work shall be new and original. The materials, equipment, and workmanship shall be of the best quality of the specified type, in conformity with Contract Documents and the best engineering and construction practices, comply with the Specifications and to the entire satisfaction of IUCAA. This requirement shall be strictly enforced at all times and stages of the Work and no request for change whatsoever shall be entertained on the grounds of anything to the contrary being the prevailing practice. The Contractor shall immediately remove from the Work any materials, equipment and/or workmanship which, in the opinion of IUCAA Estate Manager  are defective or unsuitable or not in conformity with the Contract Documents and best engineering and construction practices, and the Contractor shall replace such rejected materials, equipment and/or workmanship with proper, specified, and required and approved materials, equipment and/or workmanship, all at its own cost within a period of seven (7) days from the date of  issuance of such notice.

The Contractor shall, whenever required to do so by IUCAA Estate Manager   immediately submit satisfactory evidence and necessary test results as to the kind and quality of the materials and equipment.

21.2 Special makes or brands:  Where special makes or brands are called for, they shall be mentioned as a standard brand or make. Others brands or special makes of equivalent quality may be used provided the substituted materials are equivalent to the brand specified, and prior approval for the use of such substituted materials is obtained in writing from IUCAA Estate Manager. Unless substitutions are approved by the IUCAA in writing in advance, no deviations from the Specifications and other Contract Documents shall be permitted. The Contractor shall indicate and submit written evidence of the substituted material or equipment called for in the Specifications and other Contract Documents that

are not obtainable for incorporation in the Work within the time limit of the Contract. Failure to indicate this in writing within two weeks of the signing of the Contract will be deemed as sufficient cause for denial of any request for an extension of time because of the same. Alternative equivalent brands if suggested by the Contractor during construction may be considered provided the suggested brand fully meets the requirements and is acceptable to IUCAA. Any variation in price due to the use of alternate brands shall be permissible provided it is pre-approved in writing by the Owner’s Representative’s.

21.3 Proper scheduling and delivery of materials: All materials and equipment shall be scheduled and delivered so as to ensure a speedy and uninterrupted progress of the Work, and the same shall be properly stored.

21.4 List of Materials: Within seven (7) days of the signing of the Contract, the Contractor shall submit for the approval of the IUCAA a complete list of all materials and equipment the Contractor and its Sub-Contractors propose to use in the Work, of definite brands or makes, which differ in any respect from those specified, or the

particular brand where more than one is specified as standard. The Contractor shall also list items not specifically mentioned in the Contract Documents but which are reasonably inferred and are necessary for the proper execution and successful completion of the Work.

21.5 Right Type of Workmen, Plant And Machinery, Jigs, Tools, Etc.:  The Contractor shall employ the right type of workmen, plant and machinery, jigs, tools etc. to fabricate and/or install all materials and equipment. Such material and equipment shall be fabricated and/or installed without any damage and in accordance with the material/ equipment manufacturer's instructions and manuals, and to the satisfaction of IUCAA Estate Manager.

21.6 Inspection:  All materials, equipment, and workmanship shall be subject to inspection, examination and testing at all times and stages during construction, manufacture and/or installation, by IUCAA Estate Manager and they shall have the right to reject and order the removal and replacement of any defective material, equipment and / or workmanship or require its correction and rectification. The Contractor shall not proceed with any operation or sequence or trade of the Work until the previous operation or sequence or trade has been inspected and approved by IUCAA. No embedded items or any other work shall be covered up unless these have been inspected and approved by IUCAA Estate Manager. The onus shall be on the Contractor to get such inspections carried out and obtain such approvals. Should the Contractor fail to comply with these requirements, then all additional or redoing of work necessitated as a consequence thereof shall be at the Contractor's cost and expense. No inspection or approval shall relieve the Contractor of any of its responsibilities, obligations and liabilities under the Contract. No defective workmanship shall be repaired or patched up in any way without inspection and direction of IUCAA Estate Manager.

Rejected workmanship shall be immediately corrected and rectified and rejected materials and equipment shall be removed and replaced with proper, specified and required materials and equipment, by the Contractor to the approval and satisfaction of IUCAA. The cost of all such correction and rectification and such removal and replacement shall be to the account of the Contractor and shall be borne by him, and also, the Contractor shall be responsible for all delays in this regard. The Contractor shall promptly segregate and remove the rejected materials and equipment from the Site and shall not reuse them in the Work. If the Contractor fails to proceed at once with the correction and rectification of rejected workmanship and/or the removal and replacement of rejected materials and equipment, the Owner shall have the right to employ other persons / agencies to correct and rectify such workmanship and/or remove and replace such materials and equipment, and recover the cost there of from the Contractor, or the Owner may terminate the right of the Contractor to proceed further with the Work.

The Contractor shall furnish promptly and without any charge, all facilities, access, labour, materials, plant and tools required and necessary for enabling IUCAA Estate Manager, to carry out inspections and tests in a safe and convenient manner. The Contractor shall ascertain and ensure that the facilities and

access provided for the carrying out of all inspections are completely safe in every respect and the Contractor shall be fully responsible and liable for all matters in connection with such safety.

21.7 Testing:  All the tests on materials, equipment, and workmanship that shall be necessary in connection with the execution of the Work, as decided by IUCAA and as called for in the Contract Documents, shall be

carried out at the cost of the Contractor at the place of work or of manufacture or fabrication or at the Site or at an approved testing laboratory or at all or any such places. The Contractor shall provide all transportation, assistance, instruments, machines, labour and materials as are required for the examining, measuring and testing as described above, and all expenses connected with the tests as described above shall be borne by the Contractor.

21.8 Certificates:  The Contractor shall furnish, at its own cost, test certificates for the various materials and equipment as called for. Such test certificates shall be from the manufacturer for the particular consignment/lot/piece and shall be duly authenticated by respective consultants. The details in respect of the test certificates shall be as decided by IUCAA (in consultation with consultants) for the relevant items.

21.9 As built drawings : The Contractor shall during the course of execution, prepare and keep updated a complete set of " as-on-date as built drawings” reflecting current status of construction, marked with each and every change from the Contract drawings. Three sets of "as built" drawings as agreed shall be supplied to IUCAA Estate Manager  upon completion of project, along with a soft copy of the drawings in AutoCAD format (specified version) at no extra cost to the owner.

21.10 Daily site reports:  The Contractor shall throughout the contract period, submit daily site reports to the Project Manager and the Owner’s Representative. The reports will include, but not be limited to:

i. Record of the Site progress

ii.Number of employees, workmen. Labour engaged on the Site

iii.Number of men employed on individual trades

iv. Plant and machinery at site (including an indication as to whether the plant is working or standing)

v. Notification of accidents

vi. Material received at site on that specific day

vii. Events influencing the progress of the Work

22 BUREAU OF INDIAN STANDARDS: ( BIS )  Indian Standards Specifications A reference made to any Indian Standards Specifications in the Contract Documents shall imply reference to the latest version of that Standard, including such revisions / amendments as may be issued, during the currency of the Contract, by the Bureau of Indian Standards and the corresponding clause/s therein shall hold valid in place of those referred to. The Contractor shall keep copies at the Site of all latest publications of relevant Indian Standard Specifications applicable to the Work at the Site, as listed in the Specifications.

22.1. Amendments to BIS:  If any Amendments to BIS codes is announced after finalization of the Contract the same shall be deemed to be incorporated into the specifications, wherever applicable.

22.2. Tolerances:  In case the work does not conform to the dimensions and limits of tolerances specified in the Contract Documents and/or the Indian Standard Specifications the Contractor shall be liable for all costs and expenses incurred for rectifications and/or replacements of any other Contractor's and/or Sub-Contractor's work required, in accordance with the directions of the Estate Manager, for the proper installation of the finishing elements and/or equipment, and/or for structural purposes. The Estate Manager’s decision in this respect shall be final and binding on the Contractor and Sub-Contractors, and all such costs and expenses shall be recovered from the pertinent Contractors and Sub-Contractors and shall be deducted by the Owner from any money that may be payable or that may become payable under the Contract to such pertinent Contractors and Sub-Contractors for and on behalf of the Contractor.

23 PROTECTION OF WORKS: The Contractor shall take full responsibility for the proper care and protection of the Work carried out in respect of the Project from commencement until completion and handing over of the Project to IUCAA. The Contractor shall protect and preserve the work carried out in respect of the Project in every way from any damage, fire or accident, including by providing temporary roofs, boxing or other construction as required by IUCAA. This protection shall be provided for all property on the Site as well as adjacent to the Site. The Contractor shall adequately protect, to the satisfaction of the Estate Manager, all the items of finishing work to prevent any chipping, cracking, breaking of edges or any damage of any kind whatsoever and to prevent such work from getting marked or stained or dirty. Should the Contractor fail to protect the work in respect of the Project or any part thereof and should any damage be caused to the same, the Contractor shall be responsible for all replacement and rectification, as directed by the Estate Manager, and all costs and expenses in connection with such replacement and rectification shall be to the account of the Contractor and shall be borne by it. The Contractor shall in connection with the Work provide and maintain at its own cost all lights, security guards, fencing and anything else necessary for the protection of the Work and for the safety of the public and everyone associated with the Work, all to the approval and satisfaction of the Estate Manager. All operations necessary for the execution of the Work shall be carried out so as not to interfere with the convenience of the public, or with the traffic, or the access to, use and occupation of public or private roads and footpaths or of properties whether in the possession of the Owner or of any other person. The Contractor shall hold the Owner harmless and indemnify the Owner in respect of all claims, proceedings, damages, costs, charges, and expenses whatsoever arising out of or in relation to any such matters.

24 CLEANING OF WORKS AND CLEARING OF SITE: The Contractor shall maintain the Site and all Work thereon in neat, clean and tidy-conditions at all times. The following shall be ensured by the contractor in the regard:

i. The Contractor shall remove all rubbish and debris from the Site on daily basis and as directed by the Estate Manager. Suitable steel skips shall be provided at strategic locations around the Site to receive waste and packaging materials.

ii. Just prior to the Virtual Completion of the Work, or whenever so directed by the Estate  Manager, the Contractor shall carry out all the work necessary to ensure that the Site is clear and the Work are clean in every respect, the surplus materials, debris, sheds and all other temporary structures are removed from the Site, all plant and machinery of the Contractor are removed from Site, the areas under floors are cleared of rubbish, the gutters and drains are cleared, the doors and sashes are eased, the locks and fastenings are oiled, all electrical, plumbing and other services are tested and commissioned, the keys are clearly labelled and handed to the Estate Manager, so that at the time of Virtual Completion the whole Site and the Work are left fit for immediate occupation and use, to the approval and satisfaction of the Estate Manager, and the Owner’s Representative.

iii. Should the Contractor fail to comply with the cleaning requirements, whether progressively or before completion, or fail to clear the Site as directed and required, then the Estate Manager, after giving due notice in writing to the Contractor, shall have the right to employ other persons or agencies to carry out the cleaning and/or clearing work and all costs incurred on such work shall be recovered from the

Contractor and shall be deducted by the Owner from any money that may be payable or that may become payable to the Contractor.

25 METHOD OF MEASUREMENT:  To evaluate any additional work instructed under change orders by the Estate Manager or the Owner’s Representative, the standard method of measurement shall be in accordance with the Standards laid down by Bureau of Indian Standards (IS:1200) shall be followed. However if definite methods of measurements are stipulated in the Schedule of Rates or Specifications, then the same shall supersede BIS methods and shall be followed. In the event of any dispute with regard to the method of measurement of any work, the decision of the Estate Manager shall be final and binding and no extra claims shall be entertained or allowed at any stage in this regard.

26 COVERING UP : The Contractor shall give at least 24 hours clear notice in writing to the Estate Manager before covering up any of the Work in foundations or any other such areas in order that inspection of the Work may be carried out for maintaining proper quality control. In the event of the Contractor failing to provide such notice he shall, at its own expense, uncover such Work as required to allow the inspection to be taken and thereafter shall reinstate the Work to the satisfaction of the Estate Manager.

27 PAYMENTS AND SECURED ADVANCE:

- No advance will be paid before commencing the work.

- Only two RA bills will be allowed to be raised before final billing, which should not be less than Thirty Lakhs each.

- On submission of final bill 75% of assessed bill value shall be paid on ad hoc basis and balance will be released after verification from accounts.

27.1 Running Bills :  The Contractor shall prepare measured bills as directed by the Estate Manager (detailed measurement, abstract sheet, deviation statement for ongoing and completed work, materials reconciliation statement and any specific instructions which may be given in this regard by the Estate Manager and other supporting documents) .

27.2 Payment Certificate: The Estate Manager shall issue a payment certificate within the number of working days as reflected in tender documents, from the date of the bill received from the Contractor for the value of work (net amount due to the contractor after deductions) executed by the Contractor, provided all supporting detailed measurements, purchase bills, abstract sheets and other supporting documents requested by the Estate Manager are furnished at the time of submission of such bills. Thereafter, the Contractor shall be paid by the Owner of certified amount (after deduction of applicable retention, TDS and WCT), within 15 days as per IUCAA standard terms.

27.3 Retention Money & Final Bill:  The Retention Money will be held @ 5% of the final bill value. Security Deposit will be converted to Retention amount and it will be released only after completion of defect liability period of 14 months from the date of completion of project.

Final Bill will be released only after completion of the project and duly certified by the Project consultant/ Estate Manager. Payment of final bill will be made within one month subject to submission of complete documents.

27.4 Withholding of payments:  The Estate Manager may withhold payment on account of subsequently discovered evidence, and nullify the whole or a part of any payment certificate to such extent as may be necessary to protect the Owner from loss on account of including but not limited to the following:

i. Defective work not remedied by the Contractor, Non Compliance notices not attended by the Contractor.

ii. Failure of the Contractor to make payments properly and regularly to its own workers, to its Sub-Contractors, to its suppliers.

iii. Damage by the Contractor to the work of other Contractors, Sub-Contractors or Vendors.

iv. A reasonable doubt that the Contract cannot be completed for the balance unpaid amount.

v. A reasonable doubt that the Contractor intends to leave work items incomplete.

vi. Failure of the Contractor to execute the Work in conformity with the Contract Documents.

vii. Failure of the Contractor to meet or keep-up with the approved Construction Programme on which the agreed payment schedule is based.

viii. Failure of the Contractor to comply with and fulfill all contractual obligations and liabilities  stipulated in the Contract Documents.

ix. Failure of the contractor to submit proofs of payment of necessary ESI, PF payments for his workers.

28 RECTIFICATION OF IMPROPER WORK NOTICED: If it shall appear to the Estate Manager or the Owner’s Representative during the progress of the Work that any work has been executed with unsound, imperfect or unskillful workmanship or with materials of any inferior description or that any materials or articles provided by the Contractor for the execution of the Work are unsound or of a quality inferior to that contracted for or otherwise not in accordance with the Contract, the Contractor shall, on demand in writing from the Estate Manager, specifying the work, materials or articles complained of, notwithstanding that the same may have been passed and certified by the Estate Manager, forthwith rectify or remove and reconstruct the work so specified in whole, or in part as the case may require or , remove the materials or articles so specified and provide other proper and suitable materials or articles at its own proper charge and cost and in the event of its failing to do so within a period so specified by the Estate Manager in its demand aforesaid, the Estate Manager may rectify or remove and re-execute the work or remove and replace the materials or articles complained of as the case may be by engaging a third party contractor at the risk and expense in all respects of the Contractor, and deduct the expenses from the Retention Money or any sums that may be due at any time thereafter may become due to the Contractor or from the performance bond executed by the Contractor.

29 CHANGE ORDERS:

29.1 Change in scope of work: The Owner reserves the right to alter the Scope of Work (as defined in Clause 2.6 above) and consequently the Contract Price shall be suitably adjusted for such changes by reference to the rates in the Schedule of Rates. The Estate Manager shall issue all change orders only after obtaining the prior written consent of the Owner’s Representative. The Contractor shall not proceed with additional scope of work without prior approval from Owner/ Owner’s representative through Project Consultant.

29.2 Rates for additional, altered or substituted work If the rates for the additional, altered or substituted work are not specifically provided in the Schedule of Rates then such rates shall be derived from the rates that are specified for a similar class of work in the Contract. The Estate Manager’s interpretation in consonance with the Owner as to what is a similar class of work and its decision on the method in which the rate is to be derived shall be final and binding on the Contractor. If the rates for the additional, altered or substituted work cannot be determined in the manner specified above, then the rates for such work shall be determined on the basis of actual consumption of materials, and actual use of labour and plant and machinery, as detailed below:

i. Cost of materials supplied by the Contractor, at not more than prevailing market rates, actually incorporated in the Work.

ii. Cost of labour actually used at the Site on the Work at prevailing rates of labour.

iii. Cost allocation toward the Work for the use of any plant and machinery at the Site, on actual basis.

iv. 15% of the actual costs in respect of (i), (ii), and (iii) above, towards Contractor's establishment and all other costs and overhead and profit plus taxes as applicable shall be reimbursed. Contractor's overheads and profit shall not be allowed on free issue items.

29.3 Approval from Owner/Owner’s representative:  Before the Contractor undertakes any extra work, he shall ensure that he has received a specific Change Order, signed by the Estate Manager. No additional payments shall be made to the Contractor without prior agreement and receipt of the necessary signed Change Order. Each Change Order shall clearly state the value of the additional work agreed to and signed for by the Owner. The Contractor shall at weekly  intervals submit to the Estate Manager an account giving particulars, as full and detailed as possible, of additional work ordered in writing by the Owner and which the Contractor has executed during the preceding month. If any Change Order instructed by the Estate Manager causes a delay in the completion of the Work causing the Contractor to overrun the time fixed for completion of the Work, the Owner shall agree, following joint review of the circumstances with the Estate Manager as to the extent of the delay, to postpone the time for completion of the Work by the period of delay, provided the Contractor has notified the Owner in writing, of such expected delay before such Change Order is actually issued by the Estate Manager..

30 DEDUCTIONS FOR UNCORRECTED WORK: If the Estate Manager deems it inexpedient to get corrected or rectified any work of the Contractor which is defective or damaged or of substandard quality or is generally not in accordance with the Contract Documents, then an equitable and appropriate deduction shall be made thereof from the Contract Price, and the Project consultant’s and Estate Manager’s decision in this respect shall be final and binding on the Contractor. Furthermore if, by reason of any accident, or failure, or other event occurring to, in or in connection with the Work, or any part thereof, either during the execution of the Work or during the Defects Liability Period, any remedial or other work or repair shall, in the opinion of the Estate Manager, be urgently necessary for the safety of the Work, or any part thereof, and the Contractor is unable or unwilling to immediately do such work or repair, the Owner may employ and pay other persons or agencies to carry out such work or repairs as the Estate Manager may consider necessary. If the work or repair so done by the other persons or agencies is work which, in the opinion of the Estate Manager, the Contractor was liable to do at its own expense under the Contract, then all expenses incurred by the Owner in connection with such work or repair shall be recovered from the Contractor and shall be deducted by the Owner from any money that may be payable or that may become payable to the Contractor or from the Contractor’s Performance Bond, executed by the Contractor in favour of the Owner.

31 TIME FOR COMPLETION:

31.1 Time-essence of contract: The time allowed for carrying out the Work as entered in the tender shall be strictly observed by the Contractor and shall be deemed to be of the essence of the Contract and shall be reckoned from the date of award of the Contract. The Work shall proceed with due diligence until Final Completion. The Contractor shall prepare a Construction Programme with time schedule keeping in view the completion period stipulated for specific portions of the Work and also the overall completion time and submit the same for the approval of the Estate Manager and the Project Consultant. The Contractor shall comply with the time schedule as approved by the Estate Manager and the Project Consultant. In the event of the Contractor failing to comply with the overall and individual milestones contained in the time schedules, he shall be liable to pay liquidated damages as provided for in this Contract.

31.2 Causes of delay for which claims for extension of time may be considered; The Contractor may request claim for extension of time, subject to the conditions stated herein, should he be delayed or impeded in the execution of the Work by reason of the following (decision of IUCAA authorities in this regards will be binding on the contractor):

i. Force Majeure;

ii. Any approved changes in the scope of work directed by Owner, Project consultant, which in the opinion of the Estate Manager entail the requirement of additional time for completion of the Work.

31.3 Extension of Time : If the Contractor suffers delay or incurs expense from failure on the part of the Employer to give possession in accordance with the terms of this clause the Engineer shall grant an extension of time for the completion of the works and certify such sum as in his sole opinion, shall be fair & final to cover the expense incurred which sum shall be paid by the Employer.

31.4 Permission for Extension of Time: Request for an extension of time if any, for completion of the work by the Contractor on the grounds of his having been unavoidably hindered in its execution, or any other grounds, shall be made in writing to the Engineer-in-Charge within 30 days of the date of the hindrance, on account of which he desires such extension as aforesaid, and the Engineer-in-Charge shall, if in his opinion (which shall be final) find that reasonable grounds have been shown, may authorize such extension of time as may in his opinion be necessary or proper.

31.5 Deletions or changes in the scope of the Work :  Should any deletions or changes in the scope of the Work reduce the time required to complete the Work under the Contract, then the time savings accruing from such deletions may be considered by the Estate Manager in offsetting the durations awarded for an extension of time.

32 NO FINANCIAL OR OTHER COMPENSATION FOR DELAYS BY CONTRACTOR: The Contractor shall not be entitled to any compensation for any loss suffered by him on account of delays in commencing or in executing or in completing the Work, whatever might be the cause of the delay if such delay is on account of the Contractor.

33 PROPRIETY OF EXECUTED WORK: All executed work, whether in part or in whole shall be the exclusive property of the Owner. The Estate Manager, the Owner, the Contractor or any of its Sub-Contractors or their employees or workmen or servants or agents shall not be entitled to the use of any such work except for the purpose of carrying out

subsequent work that is required to be carried out under the Contract or to complete the Project. The Owner shall have the right to occupy and take over the Work or any part thereof at any time during the progress of the Work or upon their completion, irrespective of any pending claims or disputes that the Contractor may have against the Owner.

34 INDEMNITY:

34.1 Indemnity by Contractor:   The Contractor shall indemnify, defend and hold and keep indemnified, the Owner from and against all actions, suits, claims costs, liabilities and demands brought or made against the Owner in respect of any matter or thing done or omitted to be done by the Contractor or any of its Sub-Contractor(s) or their employees, workmen, representatives, agents, servants or suppliers in the execution of or in connection with the Work or the Contractor's or Sub-Contractor's performance under this Contract and against any loss or damage to the Owner in consequence of any action or suit being brought against the Contractor or any of its Sub-Contractor(s) or their employees, workmen, representatives, agents, servants or suppliers for anything done or omitted to be done in execution of the Work and the Project Coordination Services under this Contract, including but not limited to meeting the Project milestones, noncompliance with the applicable laws and regulations of the government and local authorities, not obtaining the relevant licences and permits, infringing any patents rights and specifically regarding use, storage and disposal of hazardous materials. The obligations of the Contractor under this clause shall survive till the closure of Defects Liability period.

34.2 Indemnity by Sub-Contractors:  The Contractor shall ensure that the Sub-Contractors indemnify, defend and hold, and keep indemnified the Owner harmless from all actions, suits, claims, costs, fines, judgments and liabilities in respect of any matter or thing done or omitted to be done by the Sub-Contractors or their employees, workmen, representatives, agents, servants and suppliers in execution of or in connection with the Work or arising out of or in any way alleged to be in connection with Sub-Contractors' performance under this Contract, including but not limited to, not meeting the Project milestones, non-compliance with the applicable laws and regulations of the government and local authorities, not obtaining the relevant licences and permits, infringing any patents rights and specifically regarding the storage, use or disposal by the Sub-Contractors of hazardous materials in, on or under the Site or at any location whatsoever in connection with the Project in any way. The Sub-Contractors' responsibility under this indemnification shall also include any and all hazardous materials introduced to the Site by their agents, representatives, employees, workmen, servants and suppliers. The obligations of Sub-Contractors under this clause survive till the closure of Defects Liability period.

35 CORRECTION OF WORK BEFORE VIRTUAL COMPLETION OF WORKS: The Estate Manager and the Project consultant shall jointly conduct an extensive inspection just prior to the Virtual Completion of the Work and shall prepare a list of materials, equipment, and workmanship which are defective or damaged or of substandard quality or improperly executed or generally unacceptable due to not being in conformity with the requirements stipulated in the Contract Documents. The Contractor shall promptly remove, replace, re-execute, rectify and make good, to conform to the requirements stipulated in the Contract Documents and to the satisfaction of the Estate Manager and the Owner’s Representative all such materials, equipment, and/or workmanship included or itemised in the said list and the Contractor shall bear and pay for all expenses in connection therewith and consequent thereon and incidental thereto, including the cost for all remedial work on the work of other contractors destroyed or damaged by such removal, replacement, re-execution, rectification and making good. If the Contractor fails to remove, replace, re-execute, rectify and make good the rejected materials, equipment, and/or workmanship within a reasonable time, fixed by written notice, the Owner may employ and pay other persons or agencies to carry out such removal, replacement, re-execution, rectification and making good and all expenses incurred in connection therewith, including all damages, losses and expenses consequent thereon and incidental thereto shall be recovered from the Contractor and shall be deducted by the Owner from the Contract Price or any money that may be payable or that may become payable to the Contractor.

36 VIRTUAL COMPLETION OF WORKS:

i. The Works shall be considered as virtually complete only upon fulfilment of the procedure laid down in clause 35 above, and only after the Work has been completed in every respect in conformity with the Contract Documents and after all the systems and services have been tested and commissioned, and after the Site has been cleared and the Work cleaned in accordance with Clause 24 and when the Estate Manager has certified in writing that the Work is Virtually Complete. The Defects Liability Period shall commence from the date of such Certificate of Virtual Completion.

ii. Prior to the Virtual Completion, if the Owner decides to occupy any portion of the Work or use any part of any equipment, the same shall not constitute an acceptance of any part of the Work or of any equipment, unless otherwise so stated in writing by the Estate Manager.

iii. Prior to the issue of the Virtual Completion Certificate, the Contractor shall submit and hand-over to the Owner’s Representative the keys to all locks, all operation and maintenance manuals for systems and services, any spares called for in the Contract, and everything else necessary for the proper use and maintenance of the Work complete with all systems and services.

37 LIQUIDATED DAMAGES / PROGRAMME CHART / MILESTONES: Subject to the provision under clause 40, any unexcused delay by the supplier in maintaining its contractual obligations towards delivery of goods and performance of services shall render the supplier liable to any or all of the following sanctions:

- deduction of liquidated damages amounting to a sum of  0.5% of the total contract price of the delayed/undelivered stores/services mentioned above for every week of delay or part of a week, subject to the maximum of 5% of the value of delayed stores.

- forfeiture of its performance security and termination of the contract for default

38 PENALTY / FINE:

38.1 Non Compliance to Safety codes: If the Estate Manager notifies the Contractor of non-compliance with safety codes, the Contractor shall immediately if so directed or in any event not more than 12 hours after receipt of such notice, make all reasonable effort to correct such noncompliance.

38.2 Levy of penalty/ fines: Levy of fines-Consumption of Pan, Gutkha, Tobbacco, alcohol, drugs, etc is strictly prohibited on-site. Violation of this shall imply an immediate penalty of Rs.10,000.00 per instance and twice the amount there after Post 3rd instance, client reserves the right the terminate the contract without further notice. If the Contractor fails to do so, the Estate Manager shall have authority to levy penalty/ fines as may be determined based on the severity of the violation. The Estate Manager shall establish the list of violations and the fines associated with non-compliance of the safety codes. Each such non-compliance shall be treated as a breach of the contract.

38.3 Penalty : If the contractor fails to complete the work as per committed schedule, there shall be a penalty as per clause No.37.

38.4 Delay : In case the delay is not acceptable to the owner, owner reserves the right to terminate the contract and enter into fresh contract with other agencies at the cost of defaulting agency.

39 GUARANTEES:

i. The Contractor understands and agrees that the Owner is expressly relying and will continue to rely on the skill and judgment of the Contractor in executing the Work and remedying any defects in the Work. The Contract represents and warrants that (i) it shall perform the Work in a timely manner, in strict accordance with the Contract Documents, and consistent with generally accepted professional, construction and construction-supervision practices and standards provided by an experienced and competent professional contractor and construction supervisor rendered under the same or similar circumstances, and (ii) it is and will be responsible to the Owner for the acts and omissions of all Sub-Contractors and their respective employees, agents and invitees and all the persons performing any of the Work.

ii. Besides the guarantees required and specified elsewhere in the Contract Documents, the Contractor shall in general guarantee all work executed by the Contractor and the Sub-Contractors for a period of 12 months from the date of issue of the Virtual Completion Certificate. Those parts of the Work or equipment or installations, for which extended guarantee periods are stipulated elsewhere in the Contract Documents, shall be guaranteed for such periods that are so stipulated. The duration of the Defects Liability Period, unless specified otherwise, shall be the extent of length of such guarantee periods.

iii. The Contractor represents, warranties and guarantees to the Owner, inter alia that:

• the construction of the Project shall be approved and would be capable of use, operation, performance and maintenance for accomplishing the purpose for which it has been built and acquired.

• the Work shall comply with the Specifications, Drawings, and other Contract Documents.

• the Work shall, for a period of 12 months from the date of issue of the Virtual Completion Certificate, be free from all defects and the Project shall be of structural soundness, durability, ease of maintenance, weather tightness etc.

• the materials, workmanship, fabrication and construction shall be of specified and agreed quality and all materials shall be new.

• the Work performed for the Owner shall be free from all liens, charges, claims of whatsoever nature from any party other than the Owner.

iv. Where, during such guarantee periods as mentioned above, any material or equipment or workmanship

or generally any item of work fails to comply or perform in conformity with the requirements stipulated in the Contract Documents or in accordance with the criteria and provisions of the guarantee, the Contractor shall be responsible for and shall bear and pay all costs and expenses for replacing and/or rectifying and making good such materials, equipment, workmanship, and items of work and, in addition, the Contractor shall be also responsible for and shall bear and pay all costs and expenses in connection with any damages and/or losses suffered as a consequence of such failure.

v. All guarantees required under the Contract shall be in the format approved by the Owner and submitted to the Project consultant and the Owner by the Contractor when requesting certification of the final bill.

40 PROJECT CLOSE-OUT DELIVERABLES: The Contractor shall be responsible to provide all the Project closeout deliverables as per the Tender Documents, prior to submitting its final bill. Such deliverables shall include but not be limited to:

i. As-Built Drawings

ii. O&M Manuals;

iii. Guarantees/ Warrantees;

iv. Special warranties;

v. Extra material/ Attic stock;

vi. Operations Training for the Facilities Management staff of the Owner;

vii. Statutory approvals;

viii. Testing and commissioning reports;

ix. Contact list;

x. Handing over/ taking over certificate duly accepted by Owner.

41 DEFECTS LIABILITY:

41.1 Maintenance by contractor during Defects Liability Period: All defective items of work and defects noticed and brought to the attention of the Contractor during the Defects Liability Period shall be promptly and expeditiously attended to and replaced and/or rectified and made good by the Contractor at its own cost, to the complete satisfaction of the Estate Manager and the Project Consultant.

41.2 Replacement and/or rectification and making good by contractors of all defective materials, equipment and/or workmanship during defects liability period: The Contractor shall replace and/or rectify and make good, at its own cost, and to the satisfaction of the Estate Manager and the Owner’s Representative, all defective items of work and defects arising, in the opinion of the Estate Manager, from materials, equipment, and/or workmanship not performing or being in accordance with the Drawings or Specifications or the instructions of the Estate Manager and or other Contract Documents or the best engineering and construction practices, and which may appear or come to notice within 12 months after Virtual Completion of the Work, that is within the Defects Liability Period as per the following:

i. Any item, material or matter repaired or replaced shall receive a new Defects Liability Period of the same duration (12 months) beginning upon the date on which the said item is repaired or replaced , material or matter is returned for use to the Owner, provided that the aggregate guarantee period shall not exceed 12 months.

ii. The Contractor shall be also liable for all costs associated with damages and/or losses which are a consequence of such defective items of work and defects, and such costs shall be recouped by Estate Manager from the Contractor and shall be recovered from the Retention Money held and/or from the Contractor's final bill (if the final bill has not been certified and paid for at the time). Such defective items of work and defects as mentioned above shall, upon instruction and direction in writing of the Estate Manager and within such time as shall be specified therein, be replaced and/or rectified and made good by the Contractor at its own cost.

iii. In case of default or failure by the Contractor to replace and/or rectify and make good such defective items of work and defects, the Owner may employ and pay other persons or agencies to replace and/or rectify and make good such defective items of work and defects, and all costs, damages, losses and expenses therefore, consequent thereon and incidental thereto shall be to the account of the Contractor and such costs, damages, losses, and expenses shall be recouped by the Owner from the Contractor and shall be recovered from the Retention Money held and/or from the Contractor's final bill (if the final bill has not been certified and paid for at the time).

iv. Should the Retention Money held (and the amount in respect of the final bill if it has not been certified and paid for at the time) be insufficient to meet such costs, damages, losses and expenses, as determined by the Estate Manager and Project consultant, the Contractor shall be legally bound to pay the balance amount due under the claim to the Owner within one month of receiving notification to that effect from the Project consultant and Estate Manager. In the event of failure on the part of the Contractor to pay the balance amount due within one month as stated above, the Owner shall be entitled to invoke the performance bond and the Contractor shall raise no objection in this regard.

v. In respect of those parts of the Work for which longer guarantee periods are stipulated elsewhere in the Contract Documents, the Defects Liability Period for such parts of the Works shall be until the end of the respective guarantee period that is stipulated for each such part.

42 FINAL COMPLETION OF THE WORK:  The Work shall be considered as finally complete at the end of the Defects Liability Period subject to the Contractor having replaced and/or rectified and made good all the defective items of work and defects in accordance with clause above, to the satisfaction of the Estate  Manager, Project consultant, Owner and provided that the Contractor has performed all its obligations and fulfilled all its liabilities under the Contract, and when the Estate Manager has certified in writing that the Works are finally complete. Such Final Completion in respect of those parts of the project for which extended guarantee periods are stipulated elsewhere in the Contract Documents, shall be achieved at the end of such stipulated guarantee periods.

43 FORCE MAJEURE:

43.1 The right of the Contractor to proceed with the Work shall not be terminated because of any delay, subject to the time limits set forth in this clause, in the execution of the Work due to unforeseeable causes beyond the control and without the fault or negligence of the Contractor, or the Sub-Contractors, being Acts of God or that of the public enemy, act of terrorism restraints of Governing States, fires and floods. The following events are explicitly excluded from Force Majeure and are solely the responsibilities of the non-performing party: a) any strike, work-to-rule action, go-slow or similar labour difficulty (b) late delivery of equipment or material (unless caused by Force Majeure event), (c) economic hardship and (d) changes in applicable laws.

43.2 If the Contractor is wholly prevented from the performance of the Contract for a period in excess of thirty (30) consecutive days because of a Force Majeure, the Owner may terminate this Contract by fifteen (15) days written notice delivered to the Contractor, and if the period of the Force Majeure exceeds one hundred and twenty (120) consecutive days, the Contractor may terminate this Contract by fifteen (15) days written notice to the Owner. In the event this Contract is so terminated, the Contractor shall be paid for the costs of the Work actually executed up to the date of termination as certified by the Estate Manager. Such costs shall not include loss of profits or for any other expenses of the Contractor or Sub-Contractors such as salaries or wages of the employees or workers, hire charges for plant and machinery, expenses towards maintenance of establishment, demobilization, break charges or any other expense. Failure to agree on an equitable settlement shall be deemed to be a dispute under this Contract.

44 TERMINATION OR SUSPENSION OF THE CONTRACT BY THE OWNER:

44.1 If the Contractor shall be adjudged bankrupt or if he should make a general assignment for the benefit of its creditors, or if a receiver shall be appointed on account of its insolvency /bankruptcy, or if he should persistently or repeatedly refuse to carry out the Works diligently, or if he should fail to provide enough skilled workmen or materials or equipment or plant and machinery or tools or anything else necessary for the progress of the Work in accordance with the approved Construction Programme, or if he should fail to make prompt payments to Sub-Contractors or to suppliers for materials or equipment or to its workers, or if he should persistently disregard laws or ordinances of the Central / State or local governments or disregards the instructions of the Estate Manager or the Owner’s Representative, or if he should be guilty of a violation or breach of any provision of the Contract, or if he has abandoned the Contract, or if he has failed to commence the Work within the time specified or if he has suspended the Work, then the Owner, may without prejudice to any other right or remedy, and after giving the Contractor seven days notice in writing, terminate the Contract and take charge of all materials, equipment, tools, and plant and machinery thereon and use these as the Owner’s property for the completion of the Project. In such case the Contractor shall be entitled to receive any payment for the Work completed by him only after the Project is completed. If the amount due to the Contractor for the Work carried out by him as per the Contract terms exceeds the expenses incurred by the Owner, including for additional management and administrative services, for completing the Project and in respect of the damages and/or losses suffered by the Owner due to the Contractor's default, then such excess shall be paid to the Contractor within three months of the final completion of the Project. If such expenses for completing the Project and in respect of the damages and/or losses suffered by the Owner exceed the amount due to the Contractor, then the Contractor shall pay the difference to the Owner within one month of receiving the a notice to that effect from the Estate Manager or the Owner’s Representative. The expenses incurred by the Owner for completing the Work and in respect of the damages and/or losses suffered by him due to the Contractor's default, shall be certified by the Estate Manager and its decision on this matter shall be final and binding on the Contractor.

44.2 The Owner may terminate the Work for convenience at any time for reasons other than for cause, without prejudice to any claims that the Owner may have against the Contractor, by giving the Contractor at least seven days’ prior written notice thereof. In such event, the Owner shall pay the Contractor for such portions of the Work as are completed and properly invoiced under the provisions for final payment in Clause 30 hereof for Work performed prior to termination. In no event, shall the total payments made to the Contractor exceed the Contract Price, and, prior to full payment, the Contractor shall comply with the requirements for the release of claims and other documentation as appropriate as provided for under the provisions for final payment in Clause 30 hereof. The Owner’s sole liability to the Contractor for termination pursuant to this Clause 48.2 shall be determined in accordance with this Clause 48.2 only and the Contractor shall not be entitled to any further payments, including without limitation, loss of anticipated profits.

44.3 The Estate Manager or Project Consultant  may suspend at any time and for any reason any part of or the whole of the Work by giving at least 24hours’ written notice thereof to the Contractor, specifying the part of the Work to be suspended and the effective date of such suspension. The Contractor shall cease work on said part of the Work on the effective date of such suspension but shall continue to perform any unsuspended part of the Work. During a suspension, the Contractor shall only be reimbursed for the cost of the unsuspended Work related to (a) the Contractor’s employees whose work has been approved by the Estate Manager, and (b) such other items authorized by the Owner pursuant to a Change Order. The Owner may, at any time, authorize resumption of the suspended part of the Work by notifying the Contractor of the part of the Work to be resumed and the effective date of suspension withdrawal. The work should be properly resumed by the Contractor after receipt of such notice. The Owner’s sole liability to the Contractor for suspension shall be determined in accordance with this Clause 48.3 and any approved Change Order, and the Owner shall not be liable for any other damages, including without limitation, loss of anticipated profits.

45 INTELLECTUAL PROPERTY RIGHTS:

45.1 It is hereby acknowledged and agreed that the Owner has commissioned the Work in connection with the Project and accordingly ownership of all intellectual property rights, including but not limited to property rights in the design and in all Drawings, Specifications and documents prepared by the Project consultants, the Contractor and any Sub-Contractors or Vendors belongs and shall be assigned solely to the Owner who shall be entitled to deal with the designs, Drawings, Specifications and documents in whole or in part, in any manner in the Owner's sole discretion. The Contractor hereby disclaims any right

What so ever on these intellectual property rights in which cases the Owner shall be duly informed in that regard. This intellectual property right entitlement shall extend to any maintenance, repair and renewal, reinstatement and enlargement of the Project. The Contractor shall ensure that any provisions of this type necessary to protect the intellectual property rights of the Owner are included in all its contracts with Sub-Contractors.

45.2 All communications, whether written or oral, including but not limited to this Contract, its Annexure, Drawings, data sheets, Specifications, bills of material, sketches, calculations, designs and all other materials shall be treated as confidential and shall be the exclusive property of the Owner unless otherwise agreed in writing and must be given to the Owner upon request, but in any event all such materials shall be delivered to the Owner upon termination/expiry of this Contract.

45.3  The Contractor agrees that it and its employees, agents, Sub-Contractors and consultants shall not (without the prior written consent of the Owner) during the term of this Contract or thereafter, disclose, make commercial or other use of, give or sell to any person, firm or corporation, any information received directly or indirectly from the Owner or the Project consultant or acquired or developed in the course of the Work, Project or this Contract, including by way of example only, ideas, inventions, methods, designs, formulae, systems, improvements, prices, discounts, business affairs, trade secrets, products, product specifications, manufacturing processes, data and know-how and technical information of any kind whatsoever unless such information has been publicly disclosed by authorised officials of the Owner. The Contractor agrees that prior to assigning any employee or agent or hiring any Sub -Contractor or consultant to work on this Project, such employee, agent, Sub-Contractor or consultant shall be required to execute a document containing in substance and form, a confidentiality provision similar to this provision.

45.4 The Contractor shall not, without the Owner's prior consent:

• take any photographs or videos of the Project (or any part thereof) for use otherwise than in connection with carrying out and completion of the Project;

• write for publication, or cause, information or comment or pictures about the Project;

• supply to any third person such as actual and prospective Owners, contractors, publishers, other interested parties and the like, the designs and any articles or information relating to the Project; and

• give interviews to the press including television, radio print and the like regarding the Project or the Contractor’s involvement in the Work.

45.5 Notwithstanding the foregoing, this provision shall not limit the obligation of the Contractor to take photographs and/or videos on a regular basis for the purpose of providing the progress reports required by this Contract.

45.6 The Contractor, Sub-Contractors and their respective employees, representatives, agents, servants, workmen and suppliers shall not, during or after the termination/expiry of this Contract, disclose any information pertaining to this Contract or the Project to any person without the prior written consent of

the Owner except when called upon to do so by a valid and lawful direction or order of a statutory or Government authority or an order of a court of law or where any of the parties require production of this document and related information for establishing their respective legal rights.

46 SETTLEMENT OF DISPUTES / ARBITRATION:

46.1 All disputes and differences of any kind whatsoever arising out of or in connection with this Contract whether during the progress of the work or after their completion shall be referred in writing by the Contractor to the Owner’s Representative, and the Owner shall within 10 days from receipt make and notify its decisions thereon in writing to the Contractor.

46.2 Decisions, directions, clarifications, measurements, drawings and certificates with respect to any matter the decision for which is specially provided for by these or other special conditions to be given and made by the Owner’s Representative or by the Estate  Manager are matters which are referred to hereinafter as exempted matters and shall be final and binding upon the Contractor and shall not be set aside on account of non-observance of any formality, any omission, delay or error in proceeding in or about the same or on any other ground or for any reason and shall be without appeal. They shall be specifically excluded from the scope of arbitration proceedings hereinafter referred to. In case of any ambiguity/dispute in arising out of or related to(including the  interpretation of any of the clauses in this Tender Document/purchase order/contract, decision of the Director IUCAA or his nominee shall be final and binding on all parties.

46.3 Subject to the aforesaid in the event of any dispute or difference between the parties hereto as to the construction or operation of this Contract, or the respective rights and liabilities of the parties on any matter in question, dispute or difference on any account or as to the withholding by the Owner of any certificate to which the Contractor may claim to be and entitled to or if the Owner fails to make a decision within the aforesaid time, then and in any such case, but except in any of the exempted matters referred to in the above clause, the Contractor after 90 days of its presenting final claim on the disputed matters, may demand in writing that the dispute or difference be referred to and settled by a sole arbitrator mutually acceptable to the Owner and the Contractor. In the event the parties fail to appoint a mutually acceptable arbitrator, the parties shall approach the appropriate court for appointment of the sole arbitrator. The award of the Arbitrator, shall be final and binding on both the parties. The provision as per the Arbitration and Conciliation Act 1996 shall apply to such arbitration. The arbitration venue shall be at Pune. The procedure for the arbitration shall be determined by the arbitrator. Costs of such arbitration shall be equally shared between the Owner and the Contractor.

46.4 The Contractor shall not, except with the consent in writing of the Owner, the Project consultant, in any way delay the carrying out of the Work by reason of such matter, question or dispute being referred to arbitration but shall proceed with the work with all due diligence and shall, until the decision of the arbitrator is given, abide by the decision of the Project consultant and no award of the arbitrator shall relieve the Contractor of its obligations to adhere strictly to the Owner, the Owner’s Representative’s or the Estate Manager’s instructions with regard to the actual carrying out of the Work except as specifically affected by such award.

47 GOVERNING LAW: The governing law of the Contract shall be Indian law. Any disputes related or arriving out this agreement shall be subject to the exclusive jurisdiction of courts of Pune.

48 STANDARDS OF CONDUCT:

48.1 Maintenance of appropriate Business standards The Contractor, in performing its obligations under this Contract, shall establish and maintain appropriate business standards, procedures and control, including those necessary to avoid any real or apparent impropriety or adverse impact on the interests of the Owner. The Owner will in no event reimburse the Contractor for any costs incurred for purposes inconsistent with such policies.

48.2 Compliance with laws, rules and regulations: Contractor represents, warrants, certificates and covenants that in connection with performance under this Contract that:

i. It shall, and the Work to be provided hereunder shall, comply with all applicable local, State, and Central laws, rules and regulations, including but not limited to those governing building constructions, environmental, safety of persons and property, Employees State Insurance, Workmen’s Compensation, Provident Fund and applicable industrial/labour laws, and land development laws, rules and regulations.

ii. No services provided hereunder will be produced using forced, indentured or convicted labour or using the labour of persons in violation of the minimum working age law in the country where the Work are rendered;

iii. It shall comply with all laws regarding improper or illegal payments, gifts or gratuities; and Contractor agrees not to pay, promise to pay or authorize the payment of any money or anything of value, directly or indirectly, to any person or entity for the purpose of illegally or improperly inducing a decision or obtaining or retaining business or any advantage in connection with this Contract;

iv. It has not paid or provided and shall not pay, any gratuity for the benefit of any agent, representative or employee of the Owner other than in accordance with the Owner’s applicable policies; and

v. It has not, and shall not, engage in any sharing or exchange of prices, costs or other competitive information or take any other collusive conduct with any third party supplier or bidder in connection with the preparation or submission of any bid or proposal to the Owner or the negotiation of this Contract.

vi. It will also comply with all rules and regulations of the Owner which may be in effect at the Facility site regarding employment, passes, badges, smoking, fire prevention, safety and conduct or property. On

behalf of the Owner, Contractor shall request and monitor that any Contractor, Sub-Contractors, vendors and each of their employees observe such.

49. Tender Validity : The tenders shall remain valid for acceptance for a period of 90 days (Ninety days) after the date of tender opening prescribed in the tender document. Any tender valid for a shorter period shall be treated as unresponsive and rejected.

50 Signing and Sealing of Tender  :  The tenderers shall submit their tenders as per tender clause.

- The original copies of the tender shall either be typed or written in indelible ink and the same shall be signed by the tenderer or by a person(s) who has been duly authorized to bind the tenderer to the contract. The letter of authorization shall be by a written power of attorney, which shall also be furnished along with the tender.

- All the copies of the tender shall be duly signed at the appropriate places as indicated in the tender documents and all other pages of the tender including printed literature, if any shall be initialed by the same person(s) signing the tender. The tender shall not contain any erasure or overwriting, except as necessary to correct any error made by the tenderer and, if there is any such correction, the same shall be initialed by the person(s) signing the tender.

iii.The tenderer is to seal the original copy of the tender in separate envelopes writing the address of the purchaser and the tender reference number on the envelope. The sentence “NOT TO BE OPENED” before 09th August, 2012 (the tenderer is to put the date & time of tender opening) are to be written on these envelopes. The inner envelopes are then to be put in a bigger outer envelope, which will also be duly sealed, marked etc. as above. If the outer envelope is not sealed and marked properly as above, the purchaser will not assume any responsibility for its misplacement, premature opening, late opening etc.

The envelopes must be super-scribed with the following information:

a) Tender Reference Number    b) Due Date  c) Name of the Vendor  d) Signature & Seal of Vendor    Date

TECHNICAL SPECIFICATIONS

1.0	LT SWITCH  GEARS & DISTRIBUTION BOARDS :

1.1	SCOPE :

This section shall cover supply, assembly, installation, connection, testing and commissioning of medium voltage cubicle type MV Switchgear and Distribution boards  as described in these specifications, drawings and schedule of quantities.  The distribution boards are designated as:

Main Distribution Boards

Sub Main Distribution Boards.

The unit rate per item shall include design supply, assembly, installation, connection, testing and commissioning of MV Assembly Distribution boards, with all the components in place, internal wiring, as specified in this specification, and shown on the drawing, and load schedule complete with supply and fixing of M.S. channel/ angle iron support on wall/floor etc.

In case of switchgears and panels issued by owner for erection the unit rate shall include inspection, receiving, storage, installation, field testing and commissioning activities including co- ordination with the suppliers of the switchgears. The rate shall be quoted per set of switchgears/panels as identified in the BOQ. The details of design/Constructional features of these switchgears are specified here below.

1.2	GENERAL :

1.2.1	SYSTEM DETAILS :

All the Main Panels/Motor control centers Distribution boards, Sub-Main Distribution boards, shall be suitable for operation on three phase/ single phase, 433/240 volts, 50 Hz neutral solidly grounded at transformer and short circuit level not less than 415 Volts at  50KA / 35 KA or as specified elsewhere.

The Distribution boards shall be designed to withstand tropical condition at site, with maximum expected ambient temperature of 45ºC and 100 percent humidity and dusty weather.

Enclosure of the switchboard shall have IP 54 protection for Indoor and IP 65 for outdoor unless otherwise stated.

1.2.2	STANDARDS AND CODES :

The Distribution boards shall comply with the latest edition of relevant Indian Standards and Indian Electricity Rules and Regulations.  The following Indian Standards shall be complied with –

| IS 1394 | L.V. switchgear and control gear Part-I - 1993 General rules |
| --- | --- |
| IS 5578-85 | Guide for marking of insulated conductors |
| IS 11353-85 | Guide for uniform system of marking & identification of conductors and apparatus terminals. |
| IS 2147-62 | Degree of protection provided by enclosures for low voltage switch gear and control gears. |
| IS 2675-83 | Enclosed distribution fuse boards and cutouts for Voltages not Exceeding 1000 V. |
| IS 2551-82 | Danger notice plates. |
| IS13947-1993 | Circuit breakers.(Part-II) |
| IS13947-1993 | Switches, Disconnectors, switch disconnector (Part - III) and fuse Combination units. |
| IS 1818-72 | Alternating current isolators (disconnectors) and earthing switches. |
| IS 8623-77 | Factory built assembles of switchgear and control gear for voltages upto and including 1000 V AC & 1200 V DC. |
| IS 8828 | Miniature air break circuit breakers for voltages not exceeding 1000 V. |
| IS 9926 | Fuse wires used in rewirable type Electric fuses upto 1100 Volts. |
| IS 2208 | HRC fuse links |
| IS 2705 | Current Transformers(Part- I,II & III) |
| IS 3156 | Voltage Transformers(Part- I,II & III) |
| IS 1248 | Indicating Instruments |
| IS 722 | Integrating Instruments |
| IS 13947-93 | Control devices and switching elements.(Part - 5)Section-1 |
| IS 13947-93 | Contactors and motor starter section 1 (Part-4) Electromechanical. Section - 1 |
|  | Section-1 |
| IS 3231 | Relays |
| IS 375 | Marking and arrangement of busbars Indian Electricity Act and Rules. |

1.2.3	SHOP DRAWINGS : 	Prior to fabrication of the Switchgears, Distribution boards, the contractor shall submit for Clients/Consultants approval the shop drawing, and design calculations, indicating type, size, short circuit rating of all the electrical components used, details & schedule of components & model Nos. type, rating etc., busbar size, internal wiring size, Distribution board dimension, colour, mounting detail etc. The contractor shall submit manufacturer's catalogues of the electrical components installed in the distribution.

1.2.4	INSPECTION : 	At all reasonable times during production and prior to transport of the distribution boards to site, the contractor shall arrange and provide all the facilities at their plant for inspection by Client/Consultant or authorised representative.

1.2.5	TEST CERTIFICATES : Testing of Distribution boards shall be carried out at factory and or at site as specified in Indian Standards in the presence of Clients/Consultants. The test results shall be recorded on prescribed forms. The test certificates for the test carried out at factory / at site shall be submitted in six copies to the Construction manager/Consultants for approval.

1.3	CUBICLE TYPE MV SWITCHGEARS & DISTRIBUTION BOARDS :

1.3.1	STRUCTURE :

The MV Switchgears panels and Distribution boards shall be sheet steel enclosed cubicle pattern, floor mounted free standing, totally enclosed dead front, compartmentalised multitier formation design. The panels shall be both sides extensible type with provision for bus bar extensions.  Generally all Switchgears, Panels, MDB's, SMDB's & DB's shall be of front access only & suitable for top entry of cables unless otherwise specifically specified for bottom entry.

All MS. sheet steel used in the construction of Distribution boards shall be 2mm thick and shall be folded and braced as necessary to provide a rigid support for all components.  Sheet steel shrouds and partitions shall be of minimum 2 mm thickness. Joints of any kind in sheet steel shall be seam welded, all welding slag grounded off and welding pits wiped smooth with plumber metal. The height of the panels should not be more than 2200 mm. The operating levels shall not be more than 1800 mm. The operating level of the lower most cubicle shall not be less than 450 mm.

The Panels / Distribution boards shall be totally enclosed, completely dust and vermin proof. Synthetic rubber gaskets (neoprene/DPDM) between all adjacent units and beneath all covers shall be provided to render the joints dust proof.  All doors and covers shall be fully gasketed and shall be lockable. Doors shall have concealed hinges. All the doors shall be suitably reinforced by channel to provide rigidity.

All panels and covers shall be properly fitted and secured with the frame, and holes in the panel correctly positioned. Fixing screws shall enter into holes tapped into an adequate thickness of metal or provided with bolt and nuts.  Self threading screws shall not be used in the construction of the panels/DBs etc.

A base channel of 75mm x 40mm x 5mm thick shall be provided at the bottom.  A clearance of 300mm between the floor of the Panels/ Distribution Board and the bottom of the lower most unit shall be provided.

The Panels/ Distribution boards shall be preferably arranged in multitier formation.  These shall be of adequate size with a provision of 20 Percent vacant space to accommodate future additional switch gear in addition to spare feeders presently provided.  The size of the boards shall be designed in such a way that the internal space is sufficient for hot air movement, and the electrical component do not attain temperature rise more than 40 degree Celsius.

Knockout holes of appropriate size and number shall be provided in the gland plate of Panels/Distribution board in conformity with the number, and size of incoming and outgoing conduits/cables.

Alternatively the Panels/Distribution boards shall be provided with removable undrilled gland plates (3mm thick).

The switch boards shall be designed to facilitate easy inspection, maintenance and repair.

The Panels/Distribution boards shall be sufficiently rigid to support the equipment without distortion under normal and short circuit condition. They shall be suitably braced for short circuit duty. Provision shall be made for permanently earthing the frames and other non current carrying parts of the switchgear by two independent earth connections.

1.3.2	PROTECTION CLASS  : All indoor Panels/Distribution boards shall have degree of protection conforming to class IP 54. While outdoor panels shall be weather proof dust and water tight IP-65.

1.3.3	METAL TREATMENT & FINISH : All sheet steel work used in the construction of switchboard shall undergo a process of degreasing, pickling in acid, cold rinsing, phosphating, passivating in seven tank metal treatment plant and shall be powder coated to the specified shade of IS.5 of approved colour. The total thickness of paint shall not be less than 40 microns.

1.3.4	BUS BARS :

The Bus bars shall be of three phases separate neutral and earth bar.  The busbars, and interconnection between busbars and various components shall be of high conductivity, high strength aluminium alloy complying with the requirement of grade E91E of IS 5082.  The busbar shall be of rectangular cross section designed to withstand full load current for phase busbars and half rated current for neutral busbars unless specified otherwise  and shall be extensible on both sides. The bus bar shall be rated for the rating of the main incoming breaker, but in any case not less than 200 Amp. capacity.  The busbar shall have uniform cross section through out the length.

The busbars and interconnections shall be provided with heat resistant and colour coded sleeves. The busbars shall be supported on unbreakable, non hygroscopic insulated supports of SMC supports at sufficiently close intervals to prevent busbar sag & shall effectively withstand without damage electromagnetic stresses in the event of short circuit. The neutral as well as earth bar shall also be capable of withstanding the fault level.

The busbars shall be housed in a separate compartment. The busbar shall be shrouded with 3mm thick transparent sheet to avoid any accidental contact. All busbars connections shall be done by drilling holes in busbars and connecting by chromium plated high tensile M.S. bolts, spring washer and nuts. Additional cross section of bus bars shall be provided in all Panels/ Distribution boards to cover up the holes drilled in the busbars. Spring and flat washers shall be used for tightening the bolts.

All connections between busbars and circuit breakers/ switches and between circuit breakers/switches and cable terminals shall be through solid copper strips of proper size to carry full rated current. These strips shall be insulated with insulating heat resistant paint with colour coding.

1.3.5	CIRCUIT COMPARTMENTS : Each circuit breaker shall be housed in separate compartments and shall be enclosed on all sides. Sheet steel hinged lockable door shall be duly interlocked with the breaker units in "ON" and "OFF" positions. Safety interlocks shall be provided for air circuit breaker to prevent the breaker from being drawn-out when the breaker is in "ON" position.

The door shall not form an integral part of the drawout position of the circuit breaker. All instruments and indicating lamp shall be mounted on the compartment door.  Sheet steel barrier shall be provided between the tiers in a vertical section.

1.3.6	INSTRUMENT COMPARTMENT : Separate and adequate compartment shall be provided for accommodating instruments, indicating lamps, control contactors/relays, and control Circuit breaker etc., These components shall be accessible for testing and maintenance without any danger of accidental contact with live parts of the circuit breaker units, bus bars and connections.

1.3.7	TERMINALS :	The outgoing terminals and neutral link shall be brought out to a cable alley suitably located and accessible from the panel front.  The current transformers for instruments metering shall be mounted on the terminal blocks.  No direct connection of incoming or outgoing cables to internal components of the Panels/Distribution board is permitted, only one conductor may be connected in one terminal.

1.3.8	WIREWAYS : 	A horizontal PVC wire way with screwed covers shall be provided at the top to take interconnecting control wiring between different vertical sections.

1.3.9	CABLE COMPARTMENTS : 	Cable compartments of adequate size shall be provided in the Panels/Distribution Boards for easy termination of all incoming and outgoing cables entering from bottom or top.  Adequate supports shall be provided in the cable compartments to support cables.  All outgoing and incoming feeder terminals shall be brought out to terminal blocks in the cable compartment.

1.3.10   EARTHING :	GI earth bars of suitable size but not less than 25 mm x 3 mm shall be provided in the Panels/Distribution Boards for the entire length of the panel.  The frame work of the Panels/Distribution board shall be connected to this earth bar.  Provision shall be made for connection from this earth bar to the main earthing bar coming from the earth pit on both sides of the Panels/Distribution board and to take tapping to the outgoing earthing strips to connect to the main distribution boards.

The earth continuity conductor of each incoming and outgoing feeder shall be connected to this earth bar.  The armour shall be properly connected with earthing clamp, and the clamp shall be ultimately bonded with the earth bar. CT earthing also shall be connected to this earth bar.

1.3.11   LABELS  :	Engraved PVC labels shall be provided on all incoming and outgoing feeders.  Single line circuit diagram showing the arrangements of circuit inside the Panels/DBs shall be pasted on inside of the panel door and covered with transparent laminated plastic sheet.

1.3.12   INTERNAL COMPONENTS  :

The Panels/ Distribution boards shall be equipped complete with all type of required number of circuit breakers, contactors, relays, MCB’s, meters, instruments, indicating lamps, push buttons, equipment, fittings, busbars, cable boxes, cable glands etc., and all the necessary internal connections /wiring as required and as indicated on relevant drawings. Components necessary for proper complete functioning of the Panels/Distribution boards, but not indicated on the drawings shall be supplied and installed on the distribution boards.

All parts of the Panel/Distribution boards carrying current including the components, connections, joints and instruments shall be capable of carrying their specified rated current continuously, without temperature rise exceeding the permissible values as per the relevant specifications at any part of the Panel/Distribution boards.

All units of the same rating and specifications shall be fully interchangeable.

1.4	MCB DISTRIBUTION BOARDS :

1.4.1	SCOPE : This section relates to specifications for design supply, assembly, installation, connection, testing and commissioning of lighting and power distribution boards (LPDB’s), using Miniature Circuit Breaker (MCB), Earth Leakage Circuit breaker (ELCB), Contactor, Neutral link, Earthing terminals, control switch terminals, cubicle of CRCA sheet steel housing and complete the item installation.

1.4.2	SYSTEM : The MCB distribution boards shall be suitable for   operation on 433/440 volt, 3 phase, 4 wire, 50 Hz A.C. supply system or 215/240 volt, 1 phase, 2 wire, 50 Hz A.C. supply system.

1.4.3	CONSTRUCTION  :

a)	The DB's shall be factory made and preferably of those manufacturers whose MCBs, ELCB's are to be used. General arrangement layout of the DB's shall be approved by the Construction manager/Consultant before manufacture.

b)	The DB shall be metal clad duly fabricated from 2mm (14/16 SWG) thick high quality CRCA sheet.

c)	The DB shall be cubicle, compartmentalized, wall/floor mounted and dead front operated.

d)	The DB shall be totally enclosed and made dust, vermin and weather proof such that it meets IP 54 of IS 2147 protection classification for Indoor & IP 65 for outdoor.

e)	A detachable cover plate of 2mm thick CRCA sheet to be provided on front of the board such that all live parts of the electrical accessories mounted on the board can be accessible only on removal of the said cover plate.

Further, the cover plate shall also, have suitable cut out so that dolly of the MCB's can be operated even if the cover plate is in position.  A transparent plastic protection cover shall be provided on the cut out portion of the cover plate.

The cover plate shall also provide right above the respective cut outs a suitable arrangement to label the electrical circuit details of the MCB's mounted on it as well as to affix a danger plate in legible manner.

The cover plate shall be fixed to the board with adequate size zinc passivated machine screws.

Above the detachable cover plate, one additional hinged door of 2mm thick CRCA sheet covering the MCB's etc., shall be provided with a suitable locking arrangement.

The hinged door shall be provided with a suitable gasket capable of withstanding corrosive & humid atmosphere and to meet degree of enclosure protection IP 54 as per IS: 2147.  The DB's shall undergo the process of painting as described under cubicle type main/sub main distribution boards.

f)	The DB shall have top/bottom entry arrangement for incoming and outgoing cables/conduits.

g)	All hardware to be used in manufacture of the DB shall either be of mild steel zinc passivated or otherwise be treated to prevent corrosion due to humid atmosphere.

h)	All internal electrical connections shall be carried out using 1100 volt grade, PVC insulated, Copper conductor of ISI approved make, having rated current carrying capacity to carry continuous full current of respective switch/MCB rating at operating conditions prevailing at the project site.

i)	The DB internals shall be earthed with use of copper strips running through out the length.  Size of the earthing strip shall be as shown in the respective drawing.

j)	The earthing strip shall be brought out on two sides of the DB's with bolted type earth terminating arrangement, for connecting to the building earthing grid. The earth terminal shall be of either brass or zinc passivated mild steel.

k)	All non current carrying metal surfaces of the DB's shall be adequately treated with seven tank pretreatment  process to render it free from grease, oil, oxide, dirt, etc., to make them ready to receive and hold coats of zinc chromate primer.

l) 	The DB's shall be provided with electric components and accessories as per the details shown in the drawing/BOQ for the respective electric distribution board.

1.4.4	INSPECTION  :

a)	The DB's shall be inspected and checked as per inspection manual of the DB manufacturer.

b)	Various electrical components and accessories of the DB's shall be checked as per drawing for the respective DB's.

c)	The DB's shall be checked for rigid mounting, earthing connection, proper rating & size of components, internal wiring etc.

d)	All mechanical fasteners and electrical connections shall be checked and tightened before installation.

1.4.5 	INSTALLATION  :

a)	The DB's shall be assembled and aligned together and be installed at site as per installation manual/ instruction of the DB manufacturer.

The installation shall conform to relevant Indian Standard specification and requirement of local site conditions.

b)	The DB shall be installed in surface/concealed manner at the location as shown in the respective drawings.

c)	All minor electrical and mechanical work required to be attended to on the DB shall be completed in an approved manner after installation but before energizing the DB's.

1.4.6	 TEST  :

Prior to commissioning of the DB's following tests shall be carried out.

a)	Mechanical endurance test shall be carried out by closing and opening of all the MCB's, switches etc.

b)	Insulation resistance test shall be carried out between phases and between phase to earth bus, keeping the isolating switch in open position. Similar test shall be carried out keeping the isolating switch in closed position.

c)	All the interlocks, controls and tripping mechanisms of the switch gears shall be tested for their proper functioning.

d)	Each panel shall be provided with a thermostatically controlled space heater of adequate rating and single phase plug point and cubicle illumination lamp with switch operated at 240V AC, 50 Hz.  Heaters shall have individual ON-OFF switches.

1.5	COMPONENTS  :

1.5.1 	GENERAL  : 	The type, size and rating of the components shall be as indicated on the relevant drawings.

While selection of the capacity of the components resulting from the prevailing conditions like room temperature shall be allowed for the thermal and magnetic trip rating shall be compensated for the ambient temperature.

The ratings indicated on the drawings are ratings anticipated at prevailing site condition.

1.5.2	AIR CIRCUIT BREAKERS :

The air circuit breaker shall comply with the requirements of IS: 13947-2 (1993) and shall have –

i)	A service short circuit breaking capacity shall be as specified and equal to short circuit withstand values. All short circuit ratings shall be Ics values.

ii)	A short circuit making capacity of 105 KA.

iii)	A short time withstand capacity of 50 KA for 1 second.

iv)	Mechanical and electrical endurance for 2000 operating cycles out of which 100 cycles should be for electrical endurance.

- Electrical overload performance at 6 times the rated current, 110% of the rated voltage as recovery voltage and 0.5 power factor.

vi)	Dielectric test of 2.5 KV applied for one minute on main circuits. Test evidence from a recognized independent laboratory/institution shall be furnished for compliance of the breakers with the above requirements.

vii)	Each pole of the ACB's shall be equipped with an inverse time delay thermal over current trip device and an electro magnetic instantaneous over current trip device.  The ACB's shall be equipped with under voltage trip relay.  The trip devices shall be direct acting. ACB shall be capable of providing short circuit overload and earthfault protection (in absolute values) if required, thru microprocessor based control unit sensing the true RMS values to ensure accurate measurement meeting the EMI/EMS requirement as per the standard.

viii)	Disconnecting devices of approved type shall be provided to facilitate the removal of the circuit breakers from the housing for test and maintenance purposes.

ix)	The ACB's shall be fitted with detachable type arc quenching device on each pole. The ACB's shall have auxiliary contacts for signaling, interlocking etc. The ACB's shall have slow close facilities for checking contact operation and contact gap adjustment.

x)	All contacts subject to arcing shall be tipped with arc resisting material.  Main contacts shall be silver plated to ensure reliability in service.

xi)	Isolating contacts shall be of the silver plated, multifinger, spring loaded type. Facilities shall be provided to isolate the circuit breaker for inspection purpose. Feature of contact wear inspection indicating the life of contacts shall be provided. The ACB shall have double insulation (class-II) with moving and fixed contacts totally enclosed for enhanced safety and inaccessibility to live parts. The breaker shall have three distinct positions with in the cassette as follows:

a)	`Service Position' - with main and auxiliary contacts connected.

b)	`Test Position' - with power contacts fully disconnected and control circuit contacts connected.

c)	`Isolated position' - With both power and control circuit contacts fully disconnected.

xii)	Interlocks shall be provided to –

a)	Prevent the breaker from being isolated unless it is in the OFF position.

b)	Prevent the breaker from being racked into the service position unless it is in the OFF position.

c)	Prevent the breaker from being accidentally pulled completely OFF the guide rail.

xiii)	Safety shutters of an insulation material shall be provided to prevent access to all live contacts, when the breaker is in the inspection position or completely withdrawn.

xiv)	Facilities for pad locking the safety shutters when breaker is completely withdrawn shall be provided.

Facilities shall be provided for earthing to circuit breaker.

xv)	Air circuit breaker shall be capable of clearing the maximum fault current which can occur.

- All electrical closing of breaker should be with Electrical motor wound stored energy spring closing mechanism with Mechanical indicator to provide ON/OFF status of ACB.

For all ACBs the operating handle should be provided for charging the spring in continuous action. The spring shall be released with ON/OFF push button command in one operation at the correct speed independent of operator speed. A direct mechanical coupling should indicate the ACB in ON to OFF position thus qualifying to disconnection as per the IS/IEC indicating the true position of all the contacts. One set of NO/NC potential free contacts to be provided for operation on building management system. All accessories like shunt, under voltage motorised mechanism etc shall be front mounted and can be fitted at site.

1.5.3	MOULDED CASE CIRCUIT BREAKERS (MCCB)  :

MCCBs shall satisfy the requirements of IS-13947 Part (II) and shall be of current limiting type.  MCCB shall provide type `C' protection to the contactors as per IEC 158-1B. MCCBs shall be quick make, quick break, independent manual type with trip free feature with mechanical ON, OFF, and TRIP indications.  A trip button shall be provided for tripping the breaker.

MCCB shall have electro-magnetic, under voltage and earth fault releases.

Alarm and auxiliary contacts, terminal shrouds, sliding type front operation kit with facility for door interlocking and pad locking shall be provided (ICS=ICU).

1.5.4	FUSE SWITCH UNITS  :

The fuse switch units shall be 3-pole double break type suitable for load break duty, quick make and break action.  Separate neutral link shall be provided in the switch. All fuse switch units shall be provided with hinged doors duly interlocked with operating mechanism so as to prevent opening of the door when the switch is in "ON" position and also prevent closing of the switch when the door is not properly secured. All contacts shall be silver plated and all live parts shall be shrouded. The incoming and outgoing terminals of switch shall be adequately sized to receive proper size of cables.  High rupturing capacity (HRC) fuse links  shall be provided with switch fuse units and shall be in accordance with IS: 2208-1962 and having rupturing capacity of not less than 35 MVA at 415 volts. HRC fuse links shall be provided with visible indicators to show that they have operated. The switch fuse unit shall be manufactured in accordance with IS:4047-1967 as amended to date.

1.5.5	MINIATURE CIRCUIT BREAKER  :

Miniature circuit breakers shall be quick make and break type and conform to IS:8828. The housing of MCBs shall be heat resistant and having a high impact strength. The fault current with stand capacity of MCBs shall not be less than 9000 amps, at 230 volts. The MCBs shall be flush mounted and shall be provided with trip free manual operating mechanism with mechanical "ON" and "OFF" indications.

The circuit breaker dollies shall be of the trip free pattern to prevent closing the breaker on a faulty circuit.

The MCB contacts shall be silver nickel and silver graphite alloy and tip coated with silver. Proper arc chutes shall be provided to quench the arc immediately.  MCB's shall be provided with magnetic fluid plunger release for over current and short circuit protection.

The over load or short circuit devices shall have a common trip bar in the case of DP and TPN Miniature Circuit Breakers. All the MCB's shall be tested and certified as per Indian Standards, prior to installation.

1.5.6	FUSE  :

Fuses shall be of high rupturing capacity (HRC) fuse links and shall be in accordance with relevant ISS and having rupturing capacity of not less than 35 MVA at 415 volts. The back up fuse rating for each motor/ equipment shall be so chosen that the fuse does not operate on starting of motors/equipment.

1.5.7	EARTH LEAKAGE CB/RESIDUAL CURRENT CB  :

The ELCB/RCCB shall comply with IS: 12640-1988/IEC: 1008. The ELCB/RCCB shall be current operated independent of the line voltage. ELCB/RCCB shall work on the principle of core balance transformer. The ELCB/RCCB shall be rated for current sensitivity of a min of 30mA and a max of 300 mA at 240/415 V AC. The terminals shall be protected against finger contact to IP:20 degree of protection. The ELCB/RCCB shall have a minimum of 20,000 electrical operations.

##### Testing Provision

A test device shall be incorporated to check the integrity of the earth leakage detection system and the tripping mechanism. When the unit is connected to service, pressing the test know shall trip the ELCB and the operating handle shall move to the “OFF” position.

1.5.8	CONTACTORS  :

The contactors shall meet with the requirements of IS: 2959.

The contactors shall be of MN series only

The contactors shall have minimum making and breaking capacity in accordance with utilization category AC3 and shall be suitable for minimum class II intermittent duty.

If the contactor forms part of a distribution board then a separate enclosure is not required, but the installation of the contactor shall be such that it is not possible to make an accidental contact with live parts.

1.5.9	VOLTMETER  : Voltmeter shall comply with IS-1248 (Latest edition) requirements. The dial of the meter shall be square in shape 96 x 96 Sq.mm size. The voltmeter shall be analogue type, flush pattern, with dust and moisture proof enclosure.

The voltmeter selector switch shall be arranged to provide line to line voltage reading and line to neutral voltage reading.

1.5.10 	AMMETER  : 	Ammeter shall comply with IS-1248 (Latest edition). The dial of the ammeter shall be square in shape of 96 x 96 Sq.mm size. The Ammeter shall be analoguel type, flush pattern with dust and moisture proof enclosure. The range of the ammeter shall be in accordance with 1 to 1.5 times the feeder full load current.  Separate current transformer shall be provided for all ammeters. Three way ON and OFF selector switch shall be provided for measuring current in different phases.

1.5.11	CURRENT TRANSFORMER  : Where ammeters are called for C.T's shall be provided for current measuring.  Each phase shall be provided with separate current transformer of accuracy class-I and suitable VA burden for operation of associated metering and controls.  Current transformer shall be in accordance with IS:2705 as amended up to date.

1.5.12	 ENERGY MANAGEMENT SYSTEM  :

The system monitors the energy consumption at the individual distribution boards for centralized billing. The requirements are as follows:

1.	To monitor each supply breaker Line & Phase Voltage, Current, Power, Energy, reactive power, P.F., Frequency etc. the trend of consumption, maximum demand in kVA time plot with an accuracy class of 0.5 Should be provided with RS 485 port option.

2.	Should monitor Demand parameter (KVA or KW) instantaneous demand & maximum demand, Day, Date, Time of MD occurrence.

3.	Each outgoing feeder shall be provided with electric 3 phase 4 wire/1 phase Energy meters to monitor energy parameter with tamper proof cover. Accuracy class 1.0.

4.	Computer System  -	Data so collected from the incoming and outgoing shall be integrated and recorded in the PC Pentium-IV, 1.1 GHz, 256 MB RAM, 40 GB HDD, 3.5” FDD, CD Drive – 52X, serial port and parallel port, 17” colour monitor, mouse and standard keyboard. Windows-98 version & MS-OFFICE 97.

132 Column Dot Matrix printer, UPS (Min 2 KVA), High speed control and graphic low loss data communication cable including required software for demand representative of the same. The required window based software shall also be provided for having pre-configured with screens which show mimics, trends, history, alarms and shall generated MIS reports.

Required high speed data cable/control cable & other network accessories like data converter, repeaters etc shall also be included by the bidder.

2.0	CABLES AND CABLE TRAYS :

2.1	GENERAL SCOPE  :  Supply, installation, storing, laying, fixing, jointing / termination, testing and commissioning of Medium Voltage XLPE insulated extruded PVC inner sheathed PVC overall Sheathed armoured aluminium/ copper conductor cables laid in built up trenches, directly buried underground, on cable trays, in pipes, clamped directly to wall or Structures etc. as called for in the drawing.

a)	Type  :

Medium voltage cables shall be circular, multicore annealed copper or aluminium conductor, XLPE  insulated, PVC extended inner sheated an PVC overall sheathed and steel wire armoured or steel tape armoured construction or unarmoured. The conductors of cable shall be stranded. Sector shaped stranded conductors shall be used for cables of 50 sqmm size and above. The cables shall conform to IS: 1554 part-I in all respects.

MV power cables shall be 2, 3, 3.5 or 4 cores, as required and shall have conductors made from electrical purity aluminium conductors conforming to IS: 8130-84.

Conductors shall be insulated with high quality PVC base compound.  Insulation and outer sheathing compounds shall conform to IS: 5831 - 84.

A common covering shall be applied over the laid-up cores by an extruded sheath of PVC.	Armouring of galvanised round steel wires or galvanised flat steel strips shall be provided over the inner sheath.

Outer sheath of PVC shall be extruded over the armouring cables shall be manufactured and tested in accordance with IS 1554 Part I.

Unless otherwise specified, all control cables shall be multicore, 1100V grade PVC insulated, armoured and overall PVC sheathed with stranded copper conductors of 2.5 sq.mm, conforming to IS 1554 Part I. Cores shall be identified by colour scheme of PVC insulation.

b)	Rating :

The cables shall be rated for a voltage of 1100 Volts.

c)	Core Identifications  :

Cores shall be provided with the following colour scheme of PVC insulation

1.   	Single Core	:    Green yellow for earthing.

2.   	Two Cores      	:    Red and Black, Blue & Black, Yellow & Black.

3.   	Three Cores    	:    Red, Yellow & Blue

4.   	Four Core     	:    Red, Yellow, Blue & Black

- Selection of Cable  :

- Cables sizes shall be selected considering the current carrying

capacity, voltage drop, maximum short circuit duty and the period of short circuit to meet the present and future anticipated loads.

- While deciding cable sizes, the derating factors for type and depth of laying, grouping, ambient temperature, ground temperature and soil resistivity shall be taken into account.

2.2	STANDARDS  :

The following standards and rules shall be applicable.

| IS 1554 | ( | PVC insulated (heavy duty) electric cables Part I for Working voltages upto and including 1100 V. |
| --- | --- | --- |
| IS 8130 | ( | Conductors for insulated electric cables and flexible Cords. |
| IS 3961 | ( | Recommended current ratings for cables:(Part 2) PVC Insulated and PVC sheathed heavy duty cables. |
| IS 5831 | ( | PVC insulation and sheath of electric cables. |

The individual cores shall have continuous numbering of the core all along its length and also be provided with identification ferrules at both ends.  Individual control cables shall have 20% spare cores.

PVC / XLPE cables shall be used for all electrical works to prevent flame propagation, smoke reduction and to avoid toxic gas emission in the event of a fire.  FRLS compound shall be tested rigorously for oxygen index as per ASTM D2863, acid gas generation to IEC 754-1, smoke density to ASTM D 2843 and flammability SS 424 1475 class F3, IEEE 383 and IEC 332-1.

Manufacturer's name, ISI Mark, cable size and type shall be clearly embossed at regular intervals on all cables.

2.3	INSPECTION  :

All cables shall be tested inspected at manufacturer’s works.  However upon receipt at site cables shall be checked for physical damages during transit.

2.4	JOINTS IN CABLES  : The contractor shall take care to see that all the cables received at site are apportioned to various locations in such a manner as to ensure maximum utilisation and avoidance of straight cable jointing. This apportioning shall be got approved by the Construction manager/ Consultant before the cables are cut to lengths.

Where straight joints in cable are unavoidable, the use and location of such straight joints shall be got approved by Construction manager/Consultant.

2.5	JOINTING BOXES FOR CABLES  : 	Cable joint boxes shall be of appropriate size, suitable for PVC insulated armoured cables of particular voltage rating.

2.6	JOINTING OF CABLES  : All cable joints shall be made in suitable, approved cable joint boxes, jointing of cables in the joint boxes and the filling in of compound shall be done in accordance with manufacturer's instructions and in an approved manner.  All straight joints shall be done in epoxy mould boxes with epoxy resin (Tropolin/M-Seal resin or approved equal).  All jointing accessories shall be of CCI/INCAB or approved equal.  All terminal leads of conductors shall be heavy soldered upto at least 50mm length.

All cables shall be joined colour to colour and tested for continuity and insulation resistance before jointing commences. The seals of cables shall not be removed until preparations for jointing are completed. Joints shall be finished on the same day as commenced and sufficient protection from the weather shall be arranged.  The conductors shall be efficiently insulated with high voltage insulating tape and by using spreaders of approved size and pattern.  The joints shall be completely filled with epoxy compound and tapped so as to ensure that the box is properly filled.

Epoxy compound shall be filled as follows –

Equal quantities of resin and hardener shall be mixed thoroughly by hand until the mixture is free from white patches and has uniform colour.  No water, oil or any other liquid shall be added to the mixture to make it soft as this will affect the properties of the compound. The mixture shall be used within 30-40 minutes of mixing. The surface on which epoxy compound is to be used, shall be free from dust, rust, oil, grease and shall be dry. The joint shall neither be disturbed nor moved till the epoxy compound is completely hardened. A smooth surface can be made by rubbing a damp cloth smoothly on the compound before it sets. The joints shall be painted after it has completely hardened.

Alternatively, ready mix of epoxy cable jointing compound may also be used.

2.7	CABLE MARKERS/CABLE TAGS  :

2.7.1	Cable Markers : All underground cables and cable joints shall be marked on the surface by markers generally manufactured and tested to the requirements of relevant ISS.  Approved CI cable markers shall be provided at every 30m along the route of the cables and at both ends of road crossing, indicating cable joints and cables as applicable.  Special CI markers shall be provided at all buried cable joints indicating "Electrical Cable Joints".  CI plates duly engraved with the size of the cable and the place it serves shall be tied to the cable at regular intervals of 5m for easy identification of cables.

2.7.2	Cable Tags : 	Cable tags shall be made out of 2 mm thick aluminium sheets, each tag 32 mm in dia with one hole of 2.5 mm dia. 6 mm below the periphery shall be provided for clamping the same with cables.

Cable designations are to be punched with letter/number punches and the tags are to be tied to cables with piano wires of approved quality and size. Tags shall be tied inside the panels beyond the glands as well as below the glands at cable entires. Along trays, tags are to be tied at all bends and on straight lengths, tags shall be provided at every 5 meter.

2.8	TERMINATION OF CABLES : Cable termination shall be done in terminal box or cable end box or distribution boards, or apparatus/equipments.  Terminations are to be made with mechanical gland and of the tinned nickel plated, anti- corrosive, three piece improved pattern which is to grip inner and outer PVC sheaths as well as the armour of the cable.  The cable ends or the core conductor are to be connected by solderless lugs or sockets using crimping tool of approved make for all cables.

All terminations of cable conductors and base conductors shall be mechanically and electrically sound and shall comply with the requirements of relevant Standards and Indian electricity regulations.

The connectors or connecting sockets are to have such dimensions so as to limit temperature rise.

When required the water tightness of the terminal boxes may be obtained by filling with a compound preferably plastic flame retarding and non-dripping type within the normal range of temperatures.

When the cable is cut during the course of installation the open ends are to be sealed immediately by means of self-adhesive non hygroscopic tape over a wax water seal to make an air and watertight joint.

2.9	INSTALLATION OF CABLES  :

Cable shall be laid in a manner as indicated on the drawings.  Generally cables are laid in the following manner.

i. 	In the underground masonry trench.

ii. 	On the cable tray/or on cable ladders.

iii. 	Buried underground.

iv. 	Through pipe sleeves.

Various installation methods are discussed in the following paragraphs.

Cables shall be laid by skilled and experienced workmen using adequate rollers to minimize stretching of the cable. The cable drums shall be placed on jacks before unwinding the cable. The cable drums shall be rotated in a direction as indicated by the manufacturer. Care shall be exercised in laying cables to avoid forming kinks. The drums shall be unrolled and cables run over wooden  rollers, placed at intervals not exceeding 2 meters.

2.9.1	General : All cables shall be adequately protected against any risk of mechanical damage to which they may be liable in normal conditions of service.

When cables pass through holes in metal work, precautions shall be taken to prevent abrasion of the cables on any sharp edges.

In every vertical cable ladders, channel or duct or trunking or cable trench containing cables and exceeding three meters in length, internal barriers shall be provided so as to prevent the air at the top of the unit from attaining an excessively high temperature.  In every vertical cable shaft, cable trench or any passage of cable through wall, ceiling, floor barriers against spread of fire and smoke shall be provided for compliance with IEE regulations. `Viper' CABLEMASTIC fr 903 fire resistant painting shall be applied on all power cables.

Where cable passes through walls, ceiling, floor, it shall run through sleeve of PVC pipes or hume pipes of adequate diameter.  After pulling the cable through sleeve, both the ends of the sleeve shall be sealed water tight with fire resistance material to prevent spread of fire and seepage of water.

Generally along each cable route either in trench or in cable trays/ladders or in pipe separate Two Nos. of earth strips/wires shall run exposed.

Where an installation comprises medium voltage cables as well as extra low voltage circuits, precaution shall be taken in accordance with relevant regulations and shall be physically separated by minimum of 300mm distance.

Metal sheaths and armour of all cables, metal conduits, ducts, trunking, and bare earth continuity conductors associated with such cables, which might otherwise come into fortuitous contact with other fixed metal work shall be effectively bonded there to earth so as to prevent appreciable potential difference at such possible points of contact.

2.9.2	Underground Installations  :

The cables shall be laid in an excavated trench.  The depth of the trench shall be minimum 1000 mm below the final ground level but shall be decided on the number of cables to be laid in the trench so that the vertical distance between two adjacent layers of cables shall not be less than 350mm.  The width of the trench shall be decided on the number of cables to be laid in the trench so that the distance between two adjacent cables shall not be less than one cable diameter.

a)	Width of Trench  :

- The minimum width of trench for laying single cable shall be 350 mm.

- Where more than over cable is to be laid in the same trench in horizontal formation, the width of trench shall be increased such that the inter axial spacing between the cables, except whether otherwise specified shall be at least 200 mm.

- There shall be clearance of at least 150 mm between axis of the end cables and the sides of the trench.

b)	Depth of Trench  :

- Where cables are laid in single tier formation, the total depth of the trench shall not be less than 1000 mm.

- When more than one tier of cables is unavoidable and vertical formation of laying adopted, depth of trench in (i) above shall be increased by 300 mm for each additional tier to be formed.

In addition to above, where gradients and changes in depth are unavoidable, these shall be gradual. The cables shall be protected by placing precast concrete tiles or burnt bricks over the cables on top layer of sand and for the full length of underground cables.  Where more than one cable is running in the same trench, the concrete tiles/bricks shall cover all the cables and shall project a minimum of 150mm on either side of the cables.

In any case the top layer of the cables shall be minimum 600 mm below the finished level of the ground.

The top of the cable trench shall be well compacted till the finished level of the ground and shall be approved by the Construction manager/Consultant. If required a laboratory compaction test shall be carried out in presence of the Construction manager/Consultant.

H.V., M.V., cables shall not be laid in the same trench/cable tray and/or along side of water main.

Cables under road crossings and any surfaces subjected to heavy traffic shall be protected by running them through hume pipes of suitable size.

Where cables cross one another, the cables of higher voltages shall be laid at lower level than the cable of lower voltage.

The relative position of the cables laid in the same trench shall be preserved and the cables shall not cross each other as far as possible. At all changes in direction in horizontal and vertical planes, the cable shall be bent smooth with a radius of bend not less than 15 times the diameter of the cable. Minimum 3 meters long loop shall be provided at both sides of every straight joint and 5 meters at each end of the cable. Distinguishing marks shall be made at the cable ends for identification.

Proximity to Communication Cables  :

MV Cables and communication cables shall as per as possible cross at right angles where power cables are laid in proximity to communication cables the horizontal and vertical clearance shall not normally be less than 1000 mm.

Insulation tapes of appropriate voltage and in red, yellow, and blue colors shall be wrapped just below the sockets for phase identification.

All the excavation and back fill including timbering, shoring, and pumping required for the installation of the cables shall be carried out as indicated on the drawing and as per requirements laid down elsewhere or as per Construction manager/Consultant direction.  Trenches shall be dug true to line and grades.  Back fill for trenches shall be filled in layers not exceeding 150mm. At each layer compaction test shall be carried out in presence of Construction manager / Consultant Each layer shall be properly rammed and consolidated before laying the next layer. The contractor shall restore all surfaces, roadways, side walls, curbs, walls, landscaping or other works cut for excavation to their original condition, the satisfaction of the Construction manager/Consultant. Suitable approved type cable markers shall be installed along the cable route & wherever change of direction takes place.

2.9.3	Cables Installed Inside the Building  : The cables inside the building shall be installed in one of the following manner, as indicated in the drawing & approved by the Construction manager / Consultant.

2.9.3.1	  Installed in Built-up Trench  : The cables laid on the bottom of the structural trenches shall not lay freely upon the trench bottom. They shall be raised to prevent the possibility of their coming into contact with deleterious materials.

The cables laid in the trench shall be laid on angle iron brackets/cable tray/cable ladder/cable troughs/cable racks as indicated on the drawings, and as approved by the Construction manager/Consultant. Where cables are clamped to the wall a minimum clearance of 100mm shall be maintained between wall and cable and minimum 150mm vertical clearance shall be maintained between two cables.  Where cables are laid on brackets the brackets shall not be fixed more than 500mm apart to avoid sag in the cables. Where the cables are laid on cable tray/ladder/troughs /racks, minimum 300mm distance shall be observed between adjacent tier of tray/ladder/ troughs/racks, and cable shall be fixed minimum 25mm away from the wall, and minimum of one cable diameter distance shall be observed between two adjacent cables. Cables shall be properly fixed with the tray / ladder / troughs / racks with cable tie or saddles or straps.

2.9.3.2	  Cables on Cable Trays/Ladders under the Ceiling or on Wall  :

Where cables are installed under above suspended ceiling or below ceiling or on wall, they shall be laid on a ladder/perforated G.I. cable tray and shall be run in such positions that they are not liable to be damaged by contact with the floor or the ceiling or other fixtures.

The ladder/perforated cable tray shall be properly fixed with channels, angles, tie rod, flats to the ceiling.  The metal inserts for fixing channels, angles, tie rod, flats shall be put in place while casting the slab.  If insert plates are not placed in position, Anchor fasteners shall be used to support cable trays if required.  The cable tray route shall be co-ordinated with other services to avoid crisscross of all the services.  While laying the cables on the tray minimum one cable diameter distance shall be observed between two adjacent cables about 20% space shall be kept spare for any future installation.

The trays shall be made of 2 mm thick perforated sheet having minimum 75 mm depth. The width of perforation shall be maximum 10mm spaced at maximum 20mm distance.  The width of the cable tray shall be selected so as to accommodate required number of cables to be laid on it, with minimum separation of minimum one cable diameter between two adjacent cables. The cables shall be tied with the cable tray with nylon strip/ Aluminium clamps/GI clamps.

All steel work shall be treated in accordance with the following procedure and in accordance with IS: 6005 "Code of Practice for Phosphating Iron and Steel".

Oil, grease, dirt and swab shall be thoroughly removed by emulsion cleaning.

Rusting and scale shall be removed by Pickling with dilute acid followed by washing with running water, rinsing with slightly alkaline hot water and over drying.

The phosphate coating shall be sealed by the application of two coats of ready mixed stoving type zinc chromate primer.

After application of the primer, two coats of finishing stove enameled paint shall be applied.

The final finished thickness of paint film on steel shall not be less than 50 microns and shall not be more than 100 microns.

Finish painted surface of steel shall present an aesthetically pleasing appearance free from uneven surface.

The finish painting shall be black matt as per ISS or as approved by consultants.

2.9.3.3	  Cables Installed in the Mechanical Room  :

The cable reaching the motors in the mechanical room or plant room or machines room or service area shall be laid on cable tray except where indicated in masonry underground trenches.

The cable reaching the motors shall be protected by rigid galvanized conduits up to a height of 300mm above the floor. Above that height, the cable shall be protected by means of oil tight flexible metallic G.I. conduits to the terminal box of the motor. The connection between the rigid conduit and the flexible conduit shall be done by a screwed coupling of an approved type. The flexible conduit shall be properly fixed with the terminal box of the motor by means of double hexagonal check nut.

2.10 	CABLE TRAY SPECIFICATION :

2.10.1	GI Cable tray shall be manufactured to comply with the specifications of National Electrical Code (NEC) and National Electrical Manufacturer's Association (NEMA).

Cable trays shall be of steel as per IS 226 and galvanised and the thickness of galvanization shall be not less than 80 microns.

Cable trays shall generally be of the following type  -

i. 	for power cables of medium - ladder type with voltage and high voltage slotted channels.

ii. 	for control cables and - perforated sheet extra low voltage cables steel sheet type.

Perforated cable trays shall be generally of channel type and the perforations in the trays shall be either 8 x 15mm or 10 x 20 mm oval holes. Control cables, extra low voltage cables and instrument cables shall be laid on perforated cable trays.

Ladder type cable trays shall be made out of perforated hot dip galvanised M.S. Sheet 2 mm thick. The size of the side channel/rails shall be 75x20x2mm hot dip galvanised M.S. Sheet. The size of the rungs shall be 35x15x2 mm hot dip galvanised M.S. sheet. The pitch of the rungs shall be not more than 250mm centre to centre. Rungs shall be welded to the side rails as per requirement.

Cable trays shall be of standard sizes –

Length 				2500 mm

Width               			150/300/450/600/800/1000mm as required

Flange of perforated tray 		75 x 20 x 2 mm

Rail/Flange of ladder type tray 	75 x 20 x 2 mm

Cable trays shall be hot dip galvanised, the thickness of galvanising shall be not less than 80 microns.  Quality of zinc used for galvanising shall be 98.8% purity.

2.10.2	 Accessories for Cable Trays  :

Following accessories of cable trays, as required, shall be supplied with the cable trays.

Coupler plates

Circular bends   	- Horizontal and Vertical.

Tees           		- Horizontal and Vertical.

Reducers

4-way cross

Tray covers

Fasteners.

Accessories also shall be galvanised, thickness of galvanising being not less than 80 microns.

2.11 	TESTING :

Prior to laying cables, and prior to energizing the cables, following tests shall be carried out –

2.11.1	 Insulation Resistance test between phases and phase to neutral and phase to earth with a   500V megger.

2.11.2  Continuity test of all the phases, neutral and earth continuity conductor.

2.11.3  Sheathing continuity test.

2.11.4	 Earth resistance test of all the phases and neutral.

All tests shall be carried out in accordance with relevant Indian Standard Code of practice and Indian Electricity Rules. The Contractor shall provide necessary instruments, equipments and labour for conducting the above test and shall bear all expenses in connection with such tests.  All tests shall be carried out in the presence of the Construction manager/Consultant and results shall be recorded in the prescribed forms.

2.12	STORING  : 	All the cables shall be supplied in drums. On receipt of cables at site, the cables shall be inspected and stored in drums with flanges of the cable drum in vertical position. The end of the cable shall be sealed for water tightness.

3.0	WIRING SYSTEM  :

3.1	SCOPE  : The scope of work under this section covers installation and wiring for lights, fans, exhaust fans, call bells, fan coil units, geysers and power sockets etc., The wiring shall generally be done using PVC insulated copper conductor multi strand wires FRLS in M.S./PVC conduits as called for including providing switches, sockets, plug tops, electronic fan regulators, outlet boxes etc.

3.2	STANDARDS  :

The following latest standards and rules shall be applicable:

| IS : 732 | Code of practice for electrical wiring installation (System voltage not Exceeding 1100 V). |
| --- | --- |
| IS : 1646 | Code of practice for fire safety of buildings (General) Electrical installation. |
| IS : 9537 | Conduits for Electrical installations (Part 1-4) |
| IS : 2667 | Fittings for rigid steel conduits for electrical wiring. |
| IS : 3480 | Flexible steel conduits for electrical wiring. |
| IS : 3837 | Accessories for rigid steel conduit for electrical wiring. |
| IS : 694 | PVC insulated cables. |
| IS : 6946 | Flexible (Pliable) non-metallic conduits for electrical installation. |
| IS : 1293 | Plugs and sockets outlets of rated voltage upto and including 250 V. |
| IS : 8130 | Specifications for conduits for electrical installation. |
| IS : 3854 | Switches for domestic and similar purposes. |
| IS : 3419 | Fittings for rigid non-metallic conduits. |
| IS : 4648 | Guide for electrical layout in residential building. |
| IS : 4649 | Adopters for flexible steel conduits. |
| IS : 5133 | Boxes for enclosures of the Electrical. |
| IS : 4615 | Switch socket outlets. |
| IS : 8884 | Code of practice for installation of Electric bells and call system. |
| IS : 2551 | Electric Danger notice plates. |
| IS : 3646 | Code of practice for interior illumination. |
| IS : 371 | Ceiling Roses. |
| IS : 302 | General and safety requirements for household and similar electrical appliances. |
| IS : 3043 | Code of practice for earthing. |
| IS : 5216 | Guide for safety procedures and practices in electrical work. |

Indian Electricity Act and Rules :

Regulations for the electrical equipment in buildings issued by the concerned Electrical Authorities.

All standards and codes mean the latest.

3.3	POINT WIRING FOR LIGHTS, FANS, EXHAUST & 6 AMPS CONVENIENCE SOCKETS :

3.3.1	A point wiring shall consist of the branch wiring from the distribution board together with a switch/electronic fan regulator as required, including providing conduit & accessories, pendant holder or a swan holder, or ceiling fan hook box or socket tc., with suitable termination. A point wiring shall include, in addition, the earth continuity conductor/wire from the distribution board to the earth pin/stud of the outlet/switch box/ light fitting & fans & all other such non current carrying metals shall be earthed and to the outlet points. No tee jointing or looping of wires shall be done any anywhere except at a switch box or a light fitting or a plug socket outlet.

The point wiring shall be carried out in the under mentioned manner :

3.3.1.1	 Supply, installation, fixing of conduits and Steel wire/ G.I. pull wire with necessary accessories, junction/pull/ inspection/switch boxes and outlet boxes/Fan hook box etc. However Switches, Switch plates & switch boxes are not    required for the lights which are controlled directly from the MCB DB's.

3.3.1.2	 Supplying and drawing of wires of required size including earth continuity PVC insulated   wire.

3.3.1.3	 Supply, installation and connection of flush type switches, sockets, cover plates, switch plates & fixing fan regulator, lamp holder, ceiling rose etc.,

3.3.1.4	 The point shall be complete with the branch wiring from the distribution board to the outlet point, through switch board, conduit with accessories, junction, pull/inspection boxes, control switch, socket, outlets boxes, ceiling roses, lamp holder, connector, extension cord wire, flexible conduits etc.

3.3.2	POINT RATE :

a) 	Circuit Main :

The circuit main wiring is used for connecting DB to DB using PVC wires in a conduit pipes. The circuit has phase, neutral & earth wires as mentioned in BOQ. The DB to DB wiring includes the following:

i)	Supply and installation of wiring in concealed/surface conduit using accessories, fish wire, termination & connections in DB, glands, Lungs, ferrules, junction boxes, identifications labels etc.

Circuit main will be measured in meters (RMT)

- Primary Point Wiring :

For the purpose of point wiring, the rate shall include the following:

Circuit Sub Mains

Point wiring the submain & point wiring has phase, neutral & earth wires as mention in the BOQ & Classified.

b)	SITC of piping & wiring from DB to switch board to first light point including following points

i)	SITC of canceled / surface piping using accessories & PVC wires for phase, neutral & earth as mentioned in BOQ, fish wire, termination of wires using lugs, glands, ferrules, junction box, switch, switch plate, switch box, ceiling rose, holders, connectors, adopters connecting from pipe to switch board, sadding etc. complete as per IS

ii)	The measurement is as per point.

c)	Secondary Point Wiring  :

The scope starts form one light point to another light point using conduit with all accessories as above & wiring connections etc. complete as described in primary point.

All Primary & Secondary Points shall be measured in nos.

d)	Wiring for 6/16 Amps Power Sockets for Equipment Wiring

The work for wiring of 6A/16A sockets and wiring for power outlets shall include following:

i)	Supply & installation of conduits from DB (concealed/surface) with its accessories up to the 6/16 A power point in required size of conduit.

ii)	Wiring from DB to the 6/16 A power point including earth wire of specified size.

- Supply and installation of the socket outlet with outlet boxes of approved make and Control switch of approved make.

- The classification of Primary & Secondary shall be as per b) above.

All 6/16 A, power socket outlets shall be measured in numbers.

3.4	SYSTEM OF WIRING  : Unless otherwise mentioned on the drawings, the system of internal wiring shall be as follows:

The system of wiring shall consist of single core, PVC insulated, 1100 Volt grade, stranded copper conductor wires/cables FRLS laid through concealed or exposed PVC/MS conduits as mentioned elsewhere or as directed by Construction manager /Consultant.

3.4.1	GENERAL  : 	Prior to laying and fixing of conduits and light outlet boxes, contractor shall carefully examine the layout drawings and prepare detailed shop drawings, indicating the exact location of light outlets, with distances marked, conduit routing, with sizes, No. of wires run in each conduit, control switch location etc. The contractor shall obtain the approval of all shop drawings by the Construction manager/Consultant prior to the installation of conduits. Any discrepancy noticed in the design drawings shall be brought to the notice of the Construction manager/Consultant. Any suggestions/modifications suggested by the contractor shall have the approval of Construction manager/Consultant before execution.

3.5	CONDUITS  :

3.5.1	Type of Conduit  :  Unless otherwise specified all conduits for concealed/ surface/exposed installation including conduits running above false ceiling shall be of heavy gauge rigid black enameled MS conduits.

All conduits installed below ground level or in the damp/wet area shall be `A' Class G.I. pipes.

All conduits for fire alarm system irrespective of surface or concealed shall be of MS conduits painted with post office red colour as specified in the BOQ.

3.5.2	PVC Conduits  : If specified to be provided in any special area the Non metallic conduits and accessories shall conform to IS 9537 (part 3), IS 3419 and each conduit shall bear the ISI Mark. PVC conduits shall be of black, round, heavy gauge polyvinyl chloride (PVC). The conduit shall be plain end type as specified in IS:9537 (Part-3). The conduits internal surface shall be smooth. Only approved quality factory made bends/accessories shall be used unless otherwise stated. Minimum size of conduits shall be 20 mm diameter PVC conduits shall be rigid unplasticised, heavy gauge having 1.8mm wall thickness upto 20 mm diameter conduit and 2.0 mm wall thickness for all sizes above 20mm diameter.

3.5.3	Metal Conduits  :  Conduits and Accessories shall conform to IS:9537 (Part-2). Solid drawn 16 gauge screwed steel conduits protected by black bituminous enamel shall be used in all situations except where galvanised steel conduits are called for. Where conduits for buried wiring are passing underground they shall be of galvanised steel conduit. Joints between conduits and accessories shall be securely made to ensure earth continuity.

No steel conduit less than 20mm in diameter shall be used. Conduits shall be solid drawn, lap welded, with minimum wall thickness of 1.6mm for conduits upto 20mm diameter and 2mm wall thickness for conduits having 25mm and above diameter.

The conduits shall be delivered to the site of construction in original bundles and each length of conduit shall bear the label of the manufacturer & ISI Mark (Engraved Markings) or painted markings.

Conduit accessories such as bends, coupling etc., shall be conforming to relevant Indian Standard Specifications.

The number of 1100 volt grade PVC insulated copper conductor wires that may be drawn in the conduits of various size shall be in conformity with code of practice for electrical wiring installation IS 732.

3.6	CONDUIT ACCESSORIES  :

3.6.1	PVC Conduit Bends & Collars  :  If PVC conduits are used then the PVC conduit bends & collars shall preferably be of the same make as of conduit. This shall conform to IS 9537/3412 with ISI Mark where necessary bends or diversion may be achieved by means of using bends and or circular inspection boxes with adequate and suitable inlet and outlet termination.  In case of recessed installation system, the bends shall be properly secured & flush with the finished wall surface.  Elbows shall not be used.  No bends shall have radius less than 2 1/2 times the outside diameter of the conduit.  Ready made factory bends shall be used where required.

3.6.2	M.S. Conduit Bends & Collars  : The M.S. conduit bends and collars shall be of M.S. black enameled coated having internal threading for screwed joints of the conduits.  The bends and collars shall conform to IS 2667 & having ISI mark. The conduit bends & collars shall preferably be of the same make as of conduit. The minimum radius of conduit bend shall be 2 1/2 times the outer diameter of the conduit pipe.  Where necessary conduit bends with inspection door shall be used, only factory made ready made bends shall be used.

3.6.3	PVC/Inspection/Junction/Pull Boxes  : The Inspection/pull box/junction boxes where used with PVC conduit installation shall be of heavy gauge PVC & conform to IS specification and shall match with the conduit sizes.  The box shall be of round/square rectangular shape with conduit stub projection for termination of conduit. The box shall be minimum 50mm deep and the size of box shall be suitable to pull/make necessary joints of wires inside the boxes. Extra deep boxes are preferred. The boxes shall have flush type cover. The colour of plate shall match the colour of paint of the surface where installed. The boxes shall have concealed screwed socket for fixing the ceiling rose.

3.6.4	M.S. Conduit/Junction/Pull/Inspection Boxes  : The boxes for junction/pull/inspection boxes to be used with M.S. conduit installation shall be heavy gauge black enameled M.S. boxes.  These boxes shall be manufactured in conformity with ISI specification and to match the type of conduit used.  The boxes shall be of round/square or rectangular shape and shall have minimum 50mm depth. The box shall have threaded stub projection to terminate M.S. conduits. The boxes shall have concealed screwed sockets for fixing the ceiling rose or cover plate.

3.7	SWITCH OUTLET & SOCKET OUTLET BOXES  :

3.7.1	Concealed Type outlet Boxes  : The concealed outlet boxes for switches, sockets, power outlets, telephone outlet, fan regulator etc., shall be of same make as of switches/sockets etc. to match the exact requirement of combination of outlets. The boxes shall be fabricated out of heavy gauge CRCA cold rolled carbon alloy sheet steel with zinc plating (G.I). The size of boxes should match the type of outlet/switch plate to be mounted on the box. The adequate No. & size of knockout holes shall be provided to terminate the conduits in the box. These boxes shall be standard factory made product of same make as of switch plates & sockets. Separate screwed earth terminal shall be provided in the box for earthing.

The outlet box shall be of minimum depth of 50mm. Boxes shall be suitable for grid mounting type of accessories. Long screw shall be provided to take care of the extra plaster thickness to mount the switch plates. Provision shall be made in the box & switch plate to have the minor adjustment of alignment of switch plate to plumb level.

3.7.2	Surface Type Boxes  : The boxes for mounting switches, sockets and other wiring devices shall be either moulded plastic or heavy gauge CRCA sheet steel painted to match the colour of wall. The box shall be suitable to terminate the M.S. surface conduit into the box. The size and shape of box shall match the exact type and combination of switch plates, receptacles & wiring devices. Deep boxes shall be used to facilitate easy termination of conduit & wires/cables. Separate screwed earth terminal shall be provided in the box for earthing.

3.7.3	Light Outlet Boxes  :  	For concealed PVC conduit installation the light outlet box shall be of PVC (round/square) with knock out holes, conduit projection suitable to terminate the conduit to the box.  The box shall be made of heavy gauge PVC & the sample to have the approval of Construction manager/Consultant before use.The boxes shall have concealed screwed socket to fix the ceiling rose. The boxes shall be minimum 50 mm deep.

For surface conduit installation the light outlet box shall be of black enameled M.S. boxes. The boxes shall have threaded stub projection having internal threading to terminate the conduit of different sizes. The boxes shall be minimum 50 mm deep.

3.7.4	Ceiling Fan Hook Boxes  : The ceiling fan hook box shall be fabricated of 2mm thick M.S. with adequately sized M.S. rod/hook to fix the ceiling fan.  The hook shall be concealed within the fan hook box.  The side extensions of rod shall be sufficiently long enough to provide adequate anchorage in the concrete.  The size of the box shall be such that it should be totally covered by the plastic canopy of the ceiling fan.  The box shall have anticorrosive primer coating.

3.8	COVER PLATES FOR SWITCHES & OUTLETS  :

Switches/socket/wiring devices plates shall be the same product as of switches/sockets/wiring devices.  This shall be of best quality moulded plastic grid mounting type device plates/frames and shall match with the type of switches/sockets & boxes.

3.9	COVER PLATES FOR INSPECTION/JUNCTION/PULL BOXES  :

The cover plate for PVC boxes shall be minimum 3mm thick of perspex/formica sheet cover. For M.S. boxes cover plate shall be black enameled M.S. plates.  The shape of the plate shall match that of the box.

3.10	RECEPTACLES  :	The sockets shall conform to IS 1293. Each socket shall be provided with control switch of appropriate rating.  The sockets shall be moulded type rated for 250 volts and of full 6 Amp or 16 Amp capacity as mentioned on the drawings.  The 6/16 Amps sockets shall be multipin (6 pin) automatic shutter type suitable for plugging 6 Amps/16 Amps tops. The shutter shall open when the earth pin of the plug top inserts in the socket.  Where called for the 16 Amps socket shall have indicating lamp. The socket outlets & switches shall be of grid mounting type.  Where called for sockets shall be provided with three pin plug top suitable to the socket & of the same make as of socket. The socket outlets installed outside the building/open to sky or in damp/wet areas shall of weather proof water tight type.

3.11	INDUSTRIAL TYPE SOCKETS :  The socket outlets single phase or three phase installed in basement area, kitchen etc., shall be three pin or 5 pin industrial type with MCB (Single phase or three phase) control. The socket & MCBs shall be mounted in a sheet steel enclosure and shall be the standard factory made product.

3.12	CONDUCTORS  :  All PVC insulated Copper conductor wires shall conform in all respects to standards as listed under sub-head 'Regulations and Standards' and shall be of 1100V Grade.

3.12.1	PVC insulated wires (for light & small power wiring)

a)	The PVC cables shall conform to IS: 694/1977.  For all internal wiring PVC insulated cables of 1100V grade, single core shall be used.

The conductors shall be plain annealed copper conductors complying with relevant ISS.

The conductors shall be circular stranded copper conductor.

b)	The minimum number and diameter of wires for circular stranded conductor shall meet the requirements set out in the relevant Indian Standards.

c)	The insulation shall be PVC compound complying with the requirements of relevant ISS. It shall be applied by an extrusion process and shall form a compact homogeneous body.

The thickness of PVC insulation shall be as set out in the relevant standards.

d)	The cores of all cables shall be identified by colors in accordance with the following    sequence.

Single phase  	-	Red

Three phase     	-	Red, Yellow, Blue

Neutral             	-	Black

Earth                	-	Green or Green/Yellow.

A means of identifying the manufacturer shall be provided throughout the length of cable.

3.12.2	Wire Sizes  :

Unless otherwise specified in the drawings the size of the cable/wires used for internal wiring shall be as follows:

In case of circuit wiring for lights, exhaust fans, ceiling fans, bell, convenience socket outlet points:-

2.5 Sq.mm   - From DB's to the junction boxes, FCU, first switch board etc. with no joints. In between joints may be at switches, socket outlet, light points only.

2.5 Sq.mm   - From junction boxes to lights/fan/ 6 A sockets outlets etc.

In case of power socket outlet circuit.

6.0 Sq.mm   - From D.B. 20/30 Amps Industrial type sockets.

4.0 Sq.mm   - From DBs to 16/20 Amps sockets.

The earth continuity conductor size as indicated in the drawing/BOQ shall be drawn through conduit along with other circuit cables/wires. For general guidance the size of the earth continuity conductor shall be as follows:

UNLESS OTHERWISE SPECIFIED MINIMUM SIZE OF EARTH CONTINUITY CONDUCTOR WIRES NOT FORMING PART OF THE SAME CABLE AS THE ASSOCIATED CIRCUIT CONDUCTOR, SHALL BE AS FOLLOWS:

| Nominal Cross-sectional area of largest associated copper circuit conductor in Sq.mm | Nominal Cross-sectional area of earth continuity Conductor in sq.mm (PVC insulated green colour wire). |
| --- | --- |
| 2.5 | 1.5 |
| 4.0 | 2.5 |
| 6.0 | 2.5 |
| 10.0 | 4.0 |
| 16.0 | 6.0 |
| 25.0 | 10.0 |
| 35.0 | 10.0 |
| 50.0 | 10.0 |

Separate circuit shall run for each water heater, pantry/kitchen equipment, window air conditioner, and similar outlets at location as shown on drawings.

3.13	INSTALLATION OF CONDUIT  :

3.13.1	Concealed Conduit System with PVC Conduit  :

a)	Unless otherwise Specified all wiring shall be in medium PVC gauge conduit embedded in wall, or ceiling and concealed in the false ceiling as specified in case of PVC conduit the size of the conduit shall be selected in conformity with I.S. code and as specified in the table given below. Factory made conduit bends and accessories shall be used. PVC Conduit shall be joined using coupler as supplied by the conduit supplier. The conduit in ceiling slab shall be straight as far as possible. Before the conduits are laid in the ceiling, the position of the outlet points, controls, junction boxes shall be set out clearly as per the dimensions and to minimise off-sets and bends. Before the reinforcement rods are kept in position electrical contractor should mark in paint the position of outlet points and conduit drop on the shuttering. When the outlet boxes are kept in position & before pouring the concrete, all outlet boxes shall be filled with paper to avoid entry of concrete inside the box. Conduits in ceiling shall be bonded to the reinforcement rods with Steel wire bonding wire at intervals not more than 1000mm, to secure them in position. PVC deep light outlet / pull boxes shall be provided as required. The conduit in ceiling slab shall be laid above the first layer of reinforcement rods to avoid cracks in the ceiling surface. In general the conduit shall not be laid directly on the shuttering surface to avoid cracks in the ceiling surface.

b)	Conduits Concealed in the wall shall be secured rigidly by means of steel hooks / staples at min. 750 mm intervals. Before conduit is concealed in the walls, all chases, grooves shall be neatly made to proper required dimensions using electrically/manually operated groove cutting tools to accommodate number of conduits. The outlet boxes for control switches, inspection and draw boxes shall be fixed as and when conduits are being fixed. The recessing of conduits in walls shall be so arranged as to allow atleast 12mm plaster cover on the same. All grooves, chases etc. shall be refilled with 1:4 cement mortar and finished upto wall surface before plastering of walls is taken up by the general civil contractor.  Horizontal chase in walls are not allowed.  Where, unavoidable prior permission of Construction manager/Consultant shall be obtained before making any chasing. Where conduits pass through expansion joints in the building, adequate expansion fitting or other approved devices shall be used to take care of the relative movement. Whenever the conduits terminate into Control Boxes, distribution board’s etc. conduits shall be rigidly connected to the boxes/boards with check nuts on either side of the entry. After conduits, junction boxes, outlet boxes etc. are fixed in position, their outlets shall be properly plugged with PVC stoppers or any other suitable material so that water, mortar, vermin or any other foreign materials do not enter into the conduit system. All conduit ends terminating into an outlet shall be provided with bushes of PVC or rubber after the conduit ends are properly filed to remove burrs and sharp edges. Necessary G.I./Steel wire pull wires shall be inserted into the conduit for drawing wires before concreting.  Insulated earth wires shall be run in each conduit originating from the panel board upto the Light, Socket and Switch boxes.  If the Electrical Contractor forgets to install any conduit/ boxes etc., before the plastering/ painting work is done by other agencies, he may be permitted to install the same with prior permission of Construction manager /Consultant and he shall be liable to make good the wall, floor, ceiling etc. at his own cost.

c)	Conduits shall be so arranged as to facilitate easy drawing of wires through them. Entire conduit layout shall be done in such a way as to avoid additional junction boxes other than light points. The wiring shall be done in a looping manner. All the looping shall be done in either switch boxes or outlet box. Joints in junction / pull boxes are strictly not allowed.

d)	All conduits shall be installed so as to avoid touching of steam and hot water pipes. Conduits shall be installed in such a way that the junction and pull boxes shall always be accessible for repairs and maintenance work. The location of junction/pull boxes shall be marked on the shop drawings and approved by the Construction manager/Consultant.

A separation of 200mm shall be maintained between electrical conduits and hot water lines in the building.

e)	No run of conduit shall exceed ten meters between adjacent draw in points nor shall it contain more than two right angle bends, or other deviation from the straight line.

f)	Caution shall be exercised in using the PVC conduits in location where ambient temperature is 50 degree Celsius or above.  Use of PVC conduits in places where ambient temperature is more than 60 degree C is prohibited.  The entire conduit system including boxes shall be thoroughly cleaned after completion of installations and before drawing of wires.  Conduit system shall be erect and straight as far as possible.  Traps where water may accumulate from condensation are to be avoided and if unavoidable, suitable provision for draining the water shall be made.

All jointing method shall be subject to the approval of the Construction manager/Consultant.

g)	Separate conduits shall be provided for the following system.

-	Lighting wiring

-	16 Amp power outlets.

- 	Telephone/intercom system.

- 	Fire Alarm system.

- 	Cable TV/Music system.

- 	Computer data cabling system.

- 	Equipment wiring/Cabling.

h)	Conduit Joints  :

Conduits shall be joined by means of plain couplers.  Where there are long runs of straight conduit, pull/inspection boxes shall be provided at intervals, as approved by the Construction manager/Consultant The conduits shall be thoroughly cleaned before making the joints.  In case of plain coupler joints, proper jointing material like a vinyl solvent cement (gray in color) or any material as recommended by the manufacturer shall be used.

i)	Bends in Conduit  :  	Wherever necessary, long bends or diversions may be achieved by bending the conduits or by employing normal bends.  No bends shall have radius less than 2.5 times outside diameter of the conduit.  Heat may be used to soften the PVC conduit for bending, but while applying heat to the conduit, the conduit shall be filled with sand to avoid any damage to the conduit. Kinks in the conduit bends shall not be acceptable.

j)	Bunching of Cables  :

Cables of AC supply of different phase shall be bunched in separate conduits. The number of insulated wires/cables that may be drawn into the conduits shall be as per the following table.  In this table, the space factor does not exceed 40%. However, in any case conduits having lesser than 20 mm diameter shall not be used.

MAXIMUM PERMISSIBLE NUMBER OF 1100 VOLT GRADE SINGLE CORE CABLES  THAT MAY BE DRAWN IN TO RIGID PVC CONDUITS.

| CABLE SIZE IN SQ.MM | SIZE OF CONDUITS (MM) [MAX. NO. OF CABLES |
| --- | --- |
|  | 20 | 25 | 32 | 40 | 50 |
| 1.5 | 4 | 8 | 12 | - | - |
| 2.5 | 4 | 6 | 10 | - | - |
| 4.0 | 2 | 4 | 8 | 12 | - |
| 6.0 | 1 | 4 | 6 | 8 | - |
| 10.0 | 1 | 3 | 5 | 10 | - |
| 16.0 | - | 2 | 4 | 5 | 12 |

Wires carrying current shall be so bunched in the conduit that the outgoing and return wires are drawn into the same conduit.  Wires originating from two different phases shall not be run in the same conduit.

3.13.2	Open/Surface Conduit System with M.S. Conduits  :

a)	Wherever specifically called for, surface conduit system shall be adopted with heavy gauge black enamalled. All conduits shall be of rigid MS. Conduit. All conduits and its accessories shall be of threaded type. Conduits shall run in square and Symmetrical lines. Before the conduits are installed, the exact route shall be marked at the site and approval of the Construction manager/ Consultant shall be obtained. Conduits shall be fixed by heavy gauge PVC saddles, secured by suitable rawl plugs, at an interval of not more than 1 meter. Wherever, couplers, bends, or similar fittings are used saddles shall be provided at either side at a distance of 300 mm from the centre of such fittings. Conduits shall be joined by means of screwed couplers and screwed accessories only. In long distance straight runs of conduit, inspection type couplers /junction boxes shall be provided. Threading shall be long enough to accommodate pipe to the full threaded portion of the couplers & accessories. Cut ends of conduits shall have no sharp edges nor any burrs left to avoid damage to insulation of wires.

b)	Bends in conduit runs shall be done by using pipe bending machine. Sharp bends shall be accomplished by introducing solid bends, inspection bends or PVC inspection boxes.  Radius of solid bends shall not be less than 75mm. Not less than 90 degree bend shall be used in a conduit run from outlet to outlet.

c)	Wherever conduits terminate into control boxes, outlet boxes, distribution boards etc, they shall be rigidly connected to the box with checknuts on either side  of the entry.

d)	Steel wire /fish wire shall be drawn in each conduit.

e)	Separate PVC insulated copper conductor earth wire shall be drawn in each conduit.

f)	Draw boxes shall be located at convenient location for easy drawing of wires.

g)	Every mains and submains shall run in an independent conduit with an independent earth wire of specified capacity along the entire length of conduit.

h)	The conduit to be installed shall be of ample cross section area to facilitate the drawing of wires. The diameter of the conduit shall be selected as per table specified in this specification.  But in no case it shall be less than 20 mm diameter.

i)	Entire conduit layout shall be done such as to avoid additional junctions boxes other than for outlet points.  Conduits shall be free from sharp edge and burrs. Conduits shall be laid in a neat and organized manner as directed and approved by the Construction manager/Consultant.  Conduit runs shall be planned so as not to conflict with any other services pipe, lines/duct.

j)	The conduit shall be painted with two coats of enamel paint, color as approved by the Construction manager/ Consultant after installation.

k)	If required, connection between PVC and steel conduits shall be through a junction box. Direct connection between PVC and steel conduits are not allowed.

l)	Where exposed conduits are suspended from the structure, they shall be clamped firmly and rigidly to hangers of design to be approved by the Construction manager/Consultant Where hanger supports are to be anchored to reinforced concrete, appropriate inserts and necessary devices for their fixing shall be left in position at the time of concreting, making holes and opening in the concrete will generally not be allowed.  Where inserts are not provided, contractor shall use only anchor fasteners. In case, it is unavoidable, prior permission of the Construction manager /Consultant shall be obtained to make any openings in the concrete surface.

m)	Conduit Joints:  Conduit pipes shall be joined by means of screwed couplers and screwed accessories, as per IS: 2667. The threads shall be free from grease or oil.  In long distanced straight runs of conduit, inspection type couplers at reasonable intervals shall be provided or running threads with couplers and lock nuts shall be provided. The bare threaded portion shall be treated with anti-corrosive paints. Threads on conduit pipes in all cases shall be between 11mm or 27mm long, sufficient to accommodate pipes to full threaded portion of couplers or accessories. Cut ends of conduit pipes shall have no sharp edges nor any burrs left, to avoid damage to the insulation of conductors while pulling them through such pipes.

Brass female bushes shall be used in each conduit termination in a switch box, outlet box, electrical panel or any other box.

Conduit shall be secure in each outlet box, switch box, electrical panel or any other box by means of one G.I. hexagonal lock nut and bush, outside and inside the box.

At each building expansion joints, approved oil tight double wire wound flexible steel conduit or any other approved method shall be used. This shall be united on both sides with the rigid conduits by suitable union.

Conduits installed in the plant room for mechanical  equipment shall be properly clamped with the mechanical supports, but in no case, it shall be fixed with the body of the equipment.

The connection of conduit to the mechanical equipment shall be through oil tight double wire wound flexible steel conduit.  In any case the length of the flexible conduit shall not exceed one meter. The flexible conduit shall be properly clamped with the body of the equipment. They shall not in any case be clamped to any cover/any removable parts of the equipment.

n)	Bends of Conduits  : 	All necessary bends in the system including diversion shall be done by bending pipes or by inserting suitable solid or circular inspection type normal box or similar fittings. Conduit fittings shall be avoided as far as possible on conduit system exposed to weather, where necessary, solid type fittings shall be used.  Radius of such bends in conduit pipes shall be not less than 75mm. No length of conduit shall have more than the equivalent of four quarter bends from outlet, the bends at the outlets not being counted.

o) 	Protection against Dampness: In order to minimize condensation or sweating inside the conduit, all outlets of conduit system shall be properly drained and ventilated, but in such a manner as to prevent the entry of insects, as far as possible.

p)	Protection of Conduit against Rust  : 	The outer surface of the conduits including bends, junction boxes, etc., forming part of the conduit system shall be adequately protected against rust, particularly when such system is exposed to weather. In all cases, no bare/ threaded portion of conduit pipe shall be allowed unless such bare threaded portion is treated with anti-corrosive coating or covered with approved plastic compound.

All screwed and socketed connections shall be adequately made fully water tight by the use of proper joining material i.e. white lead for metal conduits.

q)	Bunching of Cables  :	Unless otherwise specified, insulated conductors of different phases shall be bunched in separate conduit.

Wires carrying current shall be so bunched in the conduit that the outgoing and return wires are drawn in to the same conduit.  Wires originating from two different phases shall not be run in the same conduit.

The number of insulated wires/cables that can be drawn into the conduits shall be as per the following table.

MAXIMUM PERMISSIBLE NUMBER OF 1100 VOLTS GRADE SINGLE

CORE CABLE THAT CAN BE DRAWN INTO M.S. CONDUITS.

| CABLE SIZE IN SQ. MM | SIZE OF CONDUITS (MM) [MAX.NO. OF CABLES] |
| --- | --- |
|  | 20 | 25 | 32 | 40 | 50 |
| 1.5 | 5 | 10 | 14 | - | - |
| 2.5 | 5 | 8 | 12 | - | - |
| 4.0 | 3 | 6 | 10 | - | - |
| 6.0 | 2 | 5 | 8 | - | - |
| 10.0 | - | 4 | 7 | 10 | - |
| 16.0 | - | 3 | 5 | 6 | - |
| 25.0 | - | - | 3 | 4 | 6 |
| 35.0 | - | - | 2 | 3 | 5 |
| 50.0 | - | - | - | - | 4 |

3.13.3 Open / Surface conduit System with G.I. Conduits  :

As per 8.13.2 with matching accessories, elbows & threaded connections etc.

3.14	WIRING  :

3.14.1	All final branch circuits for lighting and appliances shall be single conductor cables run inside conduits.

Branch circuit conductor sizes shall be as shown in the load analysis of drawing and conforming to the requirements of the I.E. Regulations & I.S. Code.

Home runs indicated on the drawings for the final branch circuits shall be kept in a separate conduit upto the panel board via switches wherever called for. No other wiring shall be bunched in the same conduit   unless the other circuit main of same phase run in the conduit.

For each lot of wire supply, Contractor shall supply a certificate issued by the Manufacturer stating its origin, date of manufacture, constitution and standards to which it complies and the test certificates.

Looping system of wiring shall be used. Wires shall not be jointed inside the conduit or pull boxes.  Where joints are unavoidable, they shall be made through approved mechanical connectors with prior permission of Construction manager / Consultant.

Control switches shall be connected in the phase conductors only and shall be 'ON' when knob is down. Switches shall be fixed in galvanised steel boxes. Chromium plated screws shall be used.

Power wiring shall be distinctly separate from lighting wiring.

Each circuit phase wire from the distribution boards should be followed with a separate neutral wire of the same size as the circuit wire.

3.14.2	  Drawing of Conductors  :

a)	The drawing and jointing of PVC insulated copper wire and cables shall be executed with due regard to the following precautions.  While drawing wires through conduits, care shall be taken to avoid scratches and kinks which causes breakage of conductors. There shall be no sharp bends.

b)	Insulation shall be shaved off like sharpening of a pencil and it shall not be removed by cutting it square.

c)	Strands of wires shall not be cut for connecting terminals.  The terminals shall have sufficient cross sectional area to take all strands and shall be soldered.  Connecting brass screws shall have flat ends.  All looped joints shall be soldered and connected through block/connectors.  The pressure applied to tighten terminal screws shall be just adequate, neither too much nor too less. Conductors having nominal cross sectional areas exceeding 10 sq.mm. shall always be provided with cable sockets.  At all bolted terminals, brass flat washer of large area and approved steel spring shall be used.  Brass nuts and bolts shall be used for all connections.

d)	Only certified wiremen and cable jointers shall be employed to do jointing work.  All wires and cables shall bear the manufacturer's label and shall be brought to site in original packing.  For all internal wiring, PVC insulated wires of 1100 volts grade shall be used.  The sub-circuit wiring for point shall be carried out in loop system and no joints shall be allowed in the length of the conductors.  If the uses of joints connections are unavoidable due to any specific reason, prior permission, in writing, shall be obtained from the Architect.  No wire shall be drawn into any conduit, until all work of any nature, that may cause injury to wire, is completed.  Care shall be taken in pulling the wires so that no damage occurs to the insulation of wire. Before the wires are drawn into the conduits, the conduits shall be thoroughly cleaned of moisture, dust, dirt or any other obstruction by forcing compressed air through the conduits. The minimum size of PVC insulated conductor wires for all sub-circuit wiring for light points shall be 2.5 sq.mm. as indicated in the drawing.

3.14.3	Joints  :  All joints shall be made at main switches, distribution boards, socket outlets, lighting outlets and switch boxes only. No joints shall be made in conduits and in junction boxes. Conductors shall be continuous from outlet to inlet.

3.15	MAINS AND SUB-MAINS  :	Mains and sub-mains cable or wires where called for shall be of the rated capacity and approved make. Every main and sub-main wire shall be drawn into an independent adequate size conduit. An independent earth wire of the proper rating shall be provided for every single phase submain. For every 3- phase submain, 2 nos. earth wires of proper rating shall be provided alongwith the submain. The earth wires shall be fixed to conduits by means of clips at not more than 1000 mm distance. Where mains and sub- main cables are connected to switchgear, sufficient extra lengths of cable shall be provided to facilitate easy connections and maintenance.

3.16	LOAD BALANCING  :	 Load balancing of circuits in three phase installation shall be planned before the commencement of wiring and shall be strictly adhered to.

3.17	COLOUR CODE OF CONDUCTORS  :  Colour code shall be maintained for the entire wiring installation: red, yellow, blue for three phases, black for neutral, green/yellow green for earthing.

The control wire from light control switches to the light/ fan points shall be the same colour as that of the phase/ circuit wires feeding that particular loop.

3.18	EARTHING  : 	All earthing system shall be in accordance with IS 3043 code of practice for earthing. The type and size of earthing wire shall be as specified under the heading of cables. Each conduit originating from the DB to various outlets shall have one earth wire (PVC insulated copper conductor green colour wire).

3.19	TESTING OF INSTALLATION  : Before a completed installation is put into service, the following tests shall be complied with.

3.19.1	Insulation Resistance  : The insulation resistance shall be measured by applying 500 volt megger with all fuses in places, circuit breaker and all switches closed.

The insulation resistance in megohms of an installation, measured shall not be less than 50 megohms divided by the number of points on the circuit.

The insulation resistance shall be measured between

Earth to Phase

Earth to Neutral

Phase to Neutral

3.19.2 Earth Continuity Path  : The earth continuity conductors shall be tested for  electrical continuity and the electrical resistance of the same along with the earthing lead but excluding any added resistance or earth leakage circuit-breaker, measured from the connection, with the earth electrode to any point in the earth continuity conductor in the completed installation and shall not exceed one ohm.

3.19.3	Polarity of Single Pole Switches : A test shall be made to verify that every non linked, single pole switch is connected to one of the phase of the supply system.

3.20	COMPLETION CERTIFICATES : All the above tests shall be carried out in presence of Construction manager/Consultant and the results shall be recorded in prescribed forms. Any default during the testing shall be immediately rectified and that section of the installation shall be re-tested.  The completed test results forms shall be submitted to the Construction manager/Consultant for approval.

On completion of an electric installation a certificate shall be furnished by the contractor, countersigned by the certified supervisor under whose direct supervision the installation was carried out. This certificate shall be in a prescribed form as required by the local electric supply authority.

4.0	LIGHT FIXTURES :

4.1	SCOPE :Scope of work under this section shall include supply inspection/testing at suppliers/manufacturer's premises at site, receiving at site, safe storage, transportation from point of storage to point of erection, erection and commissioning  of light fittings, fixtures and accessories for back of the house area including all necessary supports, brackets, down rods and painting etc as required.

4.2	STANDARDS : The lighting and their associated accessories such as lamps, reflectors, housings, ballasts etc., shall comply with the latest applicable standards, more specifically the following:

| Electric light fittings General and safety requirements - | IS - 1913. |
| --- | --- |
| Industrial lighting fittings with metal reflectors - | IS - 1777 |
| Decorative lighting outposts - | IS - 5077 |
| Flood Lights - | IS - 10322 (Part-5,Section 5) |
| Luminaries for street lighting - | IS-10322(Partm3) |
| Bayonet lamp holders - | IS - 1258 |
| Bi-pin lamp holders for tubular- fluorescent lamps - | IS - 3323 |
| Ballasts for use in fluorescent light fittings - | IS - 1534 |
| Starters for fluorescent lamp - | IS - 2215 |
| Ballast for HP MV lamps - | IS - 6616 |
| Capacitors for use in fluorescent, HPMV & LP sodium Vapour lamps circuits | IS-1569 |
| Tubular Fluorescent lamps - | IS - 2418 (Part I) |
| High pressure mercury vapour lamps - | IS - 9900 (Part I) |
| Tungsten filament general electric lamps | IS - 418 |

4.3	 LIGHT FITTINGS-GENERAL REQUIREMENTS  :

a)	Fittings shall be designed for continuous trouble free operation under atmospheric conditions without reduction in lamp life or without deterioration of materials and internal wiring.  Outdoor fittings shall be weather - proof and rain proof.

b)	Fittings shall be so designed as to facilitate easy maintenance including cleaning, replacement of lamps/ starters etc.

c)	All fittings shall be supplied complete with lamps.  All mercury vapour and sodium vapour lamp fittings shall be complete with accessories like ballasts, power factor improvement capacitors, starters, etc.  Out door type fittings shall be provided with weather proof boxes.

d)	Fluorescent lamp fittings shall be complete with all accessories like ballasts, power factor improvement capacitors, starters capacitors for correction of stroboscopic effect.

e)	Each fitting shall have a terminal block suitable for loop-out connection by 1100 V PVC insulated copper conductor wires upto 4 sq.mm. the internal wiring should be completed by the manufacturer by means of standard copper wire and terminated on the terminal block.

f)	All hardwires used in the fitting shall be suitably plated or anodised and passivated.

g) 	Earthing Each lighting fitting shall be provided with an earthing terminal.  All metal or metal enclosed parts of the housing shall be bonded and connected to the earthing terminal so as to ensure satisfactory earthing continuity throughout the fixture.

h)	Painting/Finish All surfaces of the fittings shall be thoroughly cleaned and degreased and the fittings shall be free from scale, rust, sharp-edges, and burrs.

i)	The housing shall be stove-enameled or anodised as required.  The surface shall be scratch resistant and shall show  no sign of cracking or flaking when bent through 90 deg. over 12 mm dia mandrel.

4.3.1	Decorative Type Fittings  : Decorative fluorescent fittings shall be provided with mounting/housing channel cum reflectors of CRCA sheet steel. Stove enameled diffusers or louvers shall be translucent white polystyrene.

4.3.2	Accessories for Light Fittings Reflectors : The reflectors shall be made of CRCA sheet steel/aluminium /Silvered glass/Chromium plated sheet copper as required. The thickness of reflectors shall be as per relevant standards. Reflectors made of steel shall have stove enameled/vitreous enameled/epoxy coating finish.  Aluminium used for reflectors shall be anodised/epoxy stove enameled /mirror polished. The finish for the reflector shall be as specified.  The reflectors shall be free from scratches / blisters and shall have a smooth and glossy surface having optimum light reflecting coefficient.  Reflectors shall be readily removable from the housing for cleaning and maintenance without use of tools.

4.3.3	Lamp/Starters Holders  : Lamp holders shall have low contact resistance and shall be resistant to wear.  They shall hold lamps in position under normal conditions of shock and vibration prevalent in an industrial atmosphere. Lamp holders for fluorescent lamps shall be of spring loaded bi-pin rotor type.  Live parts of the lamp holder shall not be exposed during insertion or removal of the lamp or after the lamp has been taken out.

Lamp holders for incandescent and mercury vapour lamps shall be bayonet type upto 100 W and Edison screw type for higher wattages.

Starter holders for fluorescent lamps shall be so designed that they are mechanically robust and shall be capable of withstanding shocks during transit, installation and use.

4.3.4	Ballasts  : The ballasts shall be designed for long life and low power loss. They shall be mounted using self-locking, anti -vibration fixtures and shall be easy to remove without dismounting the fittings.  The enclosures shall be dust tight and  non-combustible.

Ballasts shall be inductive, heavy duty type, filled with thermosetting, insulating, moisture repellent polyester compound filled under pressure or vacuum.  Ballasts shall be provided with taps to set the voltage.  The ballast wiring shall be of copper and they shall be free from dust.

Separate ballast shall be provided in case of multilamp fittings, except in case of 2 x 20 W fittings.

4.3.5	Starters  : Starters shall have bi-metal electrodes and high mechanical strength.  Starters shall be replaceable without disturbing the reflector of lamps and without use of any tool. Starters shall have brass contacts and radio interference capacitor.

4.3.6	Capacitors  : The Capacitors shall have a constant value of capacitance and shall be connected across the supply of individual lamp circuits.

The capacitor shall have a value of capacitance so as to correct the power factor of its corresponding lamps circuit to 0.95 lag or better. Capacitor shall be hermetically sealed preferably in a metal enclosure to prevent seepage of impregnate and ingress of moisture.

4.3.7	Lamps  : Incandescent lamps shall be clear type unless otherwise specified.  Fluorescent lamps shall be "day-light colour" type unless otherwise specified and shall be provided with features to avoid blackening of lamp ends.

Mercury vapour lamps shall be of high pressure, colour    corrected type.

Lamps shall be capable of withstanding vibrations prevalent in an industrial atmosphere and connections at bend in wires and filament/electrodes shall not break under such circumstances.

PL Lamps shall be energy effective compact single ended light sources in 9 to 11W ratings consisting of two narrow glass tubes welded together.

The lamp shall be complete with integral glow switch starter and capacitor and two pin electrical connection.

The lamp shall be colour rendered to give warm colour impression.

The comptalux lamp shall have a long life and shall be energy efficient.

4.4	INSTALLATION  :

4.4.1	The light fixtures and fittings shall be assembled and installed in position complete and ready for service, in accordance with details, drawings, manufacturer’s instructions and to the satisfaction of the Construction manager /Consultants. Pendent fixtures specified with overall stem lengths are subject to change and shall be checked with conditions on the job and installed as directed.  All suspended fixtures shall be mounted rigid and fixed in position in accordance with drawings, instructions and to the approval of the Construction manager / Consultants. Fixtures shall be suspended true to alignment, plumb level and capable of resisting all lateral and vertical forces and shall be fixed as required.

4.4.2	All suspended light fixtures, fans etc, shall be provided with concealed suspension arrangement in the concrete slab/roof members.  It is the duty of the Contractor to make these provisions at the appropriate stage of construction.  Exhaust fans shall be fixed at location shown on drawings. They shall be wired to a plug socket outlet at a convenient location near the fan. All switch and outlet boxes, for fans and light fittings shall be bonded to earth. The recessed type fixtures shall not be supported into the false ceiling frame work.  This shall have independent support from the socket of ceiling using conduit down rods/steel chain with provision for adjusting the level of fitting.  Wires shall be connected to all fixtures through connector blocks. Wires brought out from junction boxes shall be encased in flexible pipes for connecting to fixtures concealed in suspended ceiling. The flexible pipes shall be check-nuted to the junction box with a brass bush. Double check nut at the fixture and flexible pipes, wherever used shall be of make and quality approved by the Construction manager/Consultants.

5.0	EARTHING  :

5.1	SCOPE  : All the non-current carrying metal parts  of electrical installation shall be earthed as per IS: 3043.  All equipment, metal conduits, rising main cable armour, switch gear, distribution boards, meters, all other metal parts forming part of the work shall be bonded together and connected by two separate and distinct conductors to earth electrodes. Earthing shall be in conformity with the provisions of Rules 32, 61, 62, 67 and 68 of IER 1956.

5. 2	G.I.PIPE EARTH STATION  :

G.I. pipe shall be of medium class, 40 mm dia and2.5 m length. Galvanising shall conform to relevant Indian Standards. G.I. pipe electrode shall be cut tampered at the bottom and provided with holes of 12 mm dia drilled not less than 7.5 cm from each other up to 2 M of length from bottom. The pipe electrode shall be as far as practicable embedded below permanent moisture level.  Except where rock is encountered, pipes shall be driven to a depth of at least 4.5 mtr. Where rock is encountered at a depth of less than 2.5mtr the electrode may be buried inclined to the vertical and the inclinations shall not be more than 30 deg from the vertical.  The pipe electrode shall be made of one piece.  Earth leads to the electrode shall be laid in a heavy duty GI pipe and connected to the pipe electrode with brass bolts, nuts and washers.  GI pipe shall be terminated in a wire meshed funnel.  The funnel shall be enclosed in a masonry chamber of 450 mm x 450 mm dimensions.  The chamber shall be provided with C.I. frame and CI inspection cover.  The earth station shall also be provided with a suitable permanent identification label tag.  The earth electrode shall conform to IS:3043 latest edition.  The soil around the earthing electrode shall be treated to reduce the resistivity of the soil by filling the complete depth of electrode with alternative layers of charcoal and salt.

5. 3	PLATE EARTH STATION  :

Plate electrodes shall be made of G.I./copper (CU) plate of 6mm/3mm thick and 600 x 600mm size.  The plate shall be buried vertically in ground at a depth of not less than 4.5 meters to the top of the plate, the plate being encased in charcoal to a thickness of 300 mm all round. It is preferable to bury the electrode to a depth where subsoil water is present.  Earth leads to the electrode shall be laid in a heavy duty GI pipe and connected to the plate electrode with brass bolts, nuts and washers.  A GI pipe of not less than 20 mm dia shall be clamped with bolts vertically to the plate and terminated in a wire meshed funnel. The funnel shall be enclosed in a masonry chamber of 450 mm x 450 mm dimensions. The chamber shall be provided with GI frame and CI inspection cover. The earth station shall also be provided with a suitable permanent identifications label tag. The earth electrode shall conform to IS:3043 latest edition.

5. 4	EARTHING CONDUCTORS  :

All earthing conductors shall be of high conductivity copper/or GI as specified and shall be protected against mechanical damage and corrosion. The connection of earth electrodes shall be strong secure and sound and shall be easily accessible. The earth conductors shall be rigidly fixed to the walls, cable trenches, cable tunnel, conduits and cables by using suitable clamps.

Main earth bus shall be taken from the main medium voltage panel to the earth electrodes.  The number of electrodes required shall be arrived at taking into consideration the anticipated fault on the medium voltage net work.

Earthing conductors for equipment shall be run from the exposed metal surface of the equipment & connected to a suitable point on the sub main or main earthing bus. All switch boards, distribution boards and isolators disconnect switches shall be connected to the earth bus. Earthing conductors shall be terminated at the equipment using suit able lugs, bolts, washers and nuts.

All conduits cable armouring etc., shall be connected to the earth all along their run by earthing conductors of suitable cross sectional area. The electrical resistance of earthing conductors shall be low enough to permit the passage of fault current necessary to operate a fuse/ protective device or a circuit breaker and shall not exceed 2 Ohms.

5. 5	LOCATION FOR EARTH ELECTRODE  : Normally an earth electrode shall not be situated less than 2 M from any building. Care shall be taken that excavation for earth electrode may not affect the column footings or foundation of the building. Further the location shall be such where the soil has reasonable chance of retaining moisture as far as possible. Entrances, pavements and roadways are definitely to be avoided for locating the earth electrode.

5.6	EARTHING SYSTEM  :   Main earthing grid shall be of 50 x 6 GI strip laid in a grid formation. All other equipments shall be earthed to this strip. All panels, equipments and non current carrying conductor shall be earthed through the strip/wire of suitable size.

Main panels	- 32 x 6

Main panels to sub panels	- 25 x 6

Sub panel to DB	- 25 x 3

DBs to sub DBs	- 8 SWG G.I.

Earthing system shall be mechanically robust and the joints shall be capable of retaining low resistance even after subjection to fault currents.

Joints shall be tinned, soldered and/or double riveted.  All the joints shall be mechanically and electrically continuous and effective.  Joints shall be protected against corrosion.

5. 7	TESTING  : On the completion of the entire installation, the following tests shall be conducted :

i)    	Earth resistance of electrodes.

ii)   	Impedance of earth continuity conductors.

iii)  	Effectiveness of earthing.

All meters, instruments and labour required for the tests shall be provided by the contractor. The test results shall be submitted in the prescribed tabulated form in triplicate to the consultants for approval.

5.8	LIGHTNING PROTECTION SYSTEM  :

5.8.1	SCOPE  :  The scope of work under this section covers the specifications for supply, installation, connection, testing and commissioning of lightening protection system consisting of the following:

a)     Air termination network.

b)     Roof conductors.

c)     Down conductors.

d)     Testing joint

e)     Earth termination network.

5.8.2	STANDARDS  : The lightning protection system shall comply with IS: 2309/ 1989 and Indian Electricity Act and Rules.

5.8.3	SYSTEM  :

a)	The lightning protection system shall be installed as indicated on the drawings or in case such is not available the contractor shall prepare one as per IS-2309/1989 and get the same approved by Construction manager/Consultant.

b)	As air terminals shall be installed on the highest roof of the building, the air terminals shall be joined to horizontal roof conductor by means of rivets / clamps.

c)	Roof conductor shall be laid horizontally on the roof as indicated on the drawing.

d)	Down conductor shall be installed on the vertical surface of the building.  The down conductor shall be joined with roof conductors in the method as prescribed by the code. A test joint shall be provided in the down conductor 1000 mm above the ground level at a place which is easily accessible for testing.

e)	The down conductor shall be joined with earth termination network or to the earthing station as indicated on the drawing.

f)	The earthing station and the earthing conductor shall be as per section under heading "EARTHING".

5.8.4	COMPONENT PART  :

5.8.4.1     Air Terminals and Roof Conductors  :

a)	An air termination shall consist of vertical conductor or a system of horizontal conductors and shall be installed along the outer perimeter of the roof.

b)	No part of the roof shall be more than 9 m from the nearest horizontal protective conductor.

c)	All metallic projections, chimneys, ducts, vent pipe, railings, gutters etc., on or above the main surface of the roof of the structure shall be bonded to and form part of the air termination network.  The method and nature of the fixing shall be simple, solid and permanent.

d)	The minimum dimension of the air termination network shall be as follows:

Above Ground Below Ground

Galvanised iron strip   20 x 3 mm       32 mm x 6 mm

e)	The Air terminal shall be installed vertical on the highest point of the roof and shall be clamped firmly with the structure.  The roof conductor shall be laid horizontally above the finishing of the roof surface.

5.8.4.2     Down Conductor   :

a)	The number of down conductors shall be as follows:

1)	A structure having a base area not exceeding 100 sq.m shall have only one down conductor.

2)	For a structure having a base area exceeding 100 sq.m, the number of down conductors shall equal to smaller of the following:

One, for first 100 Sq.m plus one more for every 300 sq.m or part thereof in excess of the first 100 sq.m or one for every 30 m of perimeter.

b)	The down conductor shall be distributed around the outside wall of the structure.

c)	Any external metal running vertically through the structure shall be bonded to the down conductor at the top and     bottom.

d)	A down conductor shall follow the most direct path possible between the air terminals and the earth termination.

e)	The size of the down conductor shall be similar to roof conductor/air termination network.

f)	Each down conductor shall be provided with a testing joint in such a position that, it is convenient for testing. (about 1000 mm above Ground level)

5.8.4.3    Joints and Bonds  :

a)	The lightning protection system shall have as few joints as possible.  Joints and bonds shall be mechanically and electrically effective eg. Clamped, screwed, bolted, riveted or welded. With overlapping joint, the length of overlapping shall not be less than 25mm for all types of conductor.  Contact surfaces shall be first cleaned, then inhibited from oxidation with a suitable non-corrosive compound. Joints of dissimilar metals shall be protected from moisture by an inert, tenacious material.

b)	The lightning conductor shall be secured at not more than 2 M apart for horizontal run & 1.0 M for vertical run by fasteners resistive to corrosion.

5.8.4.4   Earth Resistance  :  	The resistance from any part of the lightning protection system to earth shall not exceed 10 Ohm before any bonding has been effected to metal in or on a structure or to services below ground. If the value obtained exceeds the specified 10 Ohm it shall be reduced by adding to the number of earth electrode.

In addition the resistance from the earth electrode to the nearest test clamps shall not exceed 0.2 Ohm.

5.8.4.5   Method of Measurement   :

The complete earth conductor shall be measured and paid per unit length, including air termination network, down conductor, test joints and earthing termination network.

LIST OF APPROVED MAKES

| S.No. | Name of Item | Make Approved |
| --- | --- | --- |
| 1. | MV Boards, MCCs | Accusonic / Visa /Zenith or CPRI Approved |
| 2. | MCB Distribution Boards | Legrand / Siemens / Schinder/ L&T |
| 3. | Moulded Case Circuit Breaker/ACB | Legrand / Siemens / Schinder/ L& T |
| 4. | Miniature Circuit Breaker | Legrand / Siemens / Schinder/ L&T |
| 5. | Switch Fuse Units | L&T / Schinder / Siemens |
| 6. | Contactors and Starters | L&T / Siemens / Schinder |
| 7. | Change over Switches | HPL Sochomech / L&T |
| 8. | Current Transformer | L&T / Starlite |
| 9. | ELCB | Legrand / Siemens / Schinder |
| 10. | Push Buttons | L&T / Technic |
| 11. | Indicating Lamps | L&T / Technic |
| 12. | Fuses & Fuse bases | L&T / Siemens |
| 13. | Digital KWH Meters with RS 485 Ports | MSEDCL Approved/ Conzerv |
| 14. | Indicating / Measuring Instruments | Legrand / Conzerv |
| 15. | Terminals | Elmex / Connectwell |
| 16. | HT / LT / Telephone Cables (Power) | Finolex / Polycab/ RPG |
| 17. | PVC insulated Copper Wires | RR Cables/ Finolex / Polycab |
| 18. | Cable Glands Single/Double Compression | Braco / Dowells |
| 19. | PVC rigid conduits & Accessories | Precision/ Diamond |
| 20. | Switches, Sockets, Plugs etc | Legrand |
| 21. | Industrial sockets | Legrand / Schinder |
| 22. | Light Fitting Fluorscent /CFL /GLS | Wipro/ Philips |
| 23. | Fancy / Decorative light fittings | Tulip / Artlite |
| 24. | Ceiling Fans | C.G. / Bajaj |
| 25. | Exhaust Fans | USHA / C.G. |
| 26. | Relays | Areva / Minilec |
| 27. | Bi-metalic Crimping Type Lugs | Dowells |
| 28. | Capacitors | Vishay / Subodhan/ Shreem/ Prabhodhan |
| 29. | Cable Trays / Wireways | Legrand /CABLOFIL / Profab / Shruti |
| 30. | Bus Duct & Bus Duct Accessories | L&T / Legrand |
| 31. | Multi Function Meter | L & T / Conzerv/ HPL |
| 32. | MSEDCL approved energy meter | HPL / EMCO |
| 33. | Anchor fasteners | Hilti / Shakti |

SEAL & SIGNATURE OF THE CONTRACTOR

##### APPENDIX - III PROFORMA FOR CONTRACT AGREEMENT

ARTICLES OF AGREEMENT

ARTICLES OF AGREEMENT made at this --------- th day of ------------ 2012 between The Senior Administrative Officer, Inter University Centre For Astronomy and Astrophysics, Post Bag No. 4, Ganeshkhind, Pune - 411007 having it’s registered at the same address hereinafter called Owner. The Owner (which expression shall include its successors and assigns wherever the context or meaning shall successors and assigns wherever the context or meaning shall  M/S. ------------------------------ having their registered office at ----------------------------------------------  (Hereinafter called the Contractor) of the other part.

WHEREAS the owner is desirous of constructing their project LT ELECTRICAL WORKS FOR NEW DATA CENTRE, RESIDENTIAL & HOSTEL BLOCK AT IUCAA, PUNE and has caused the drawings, specifications and the bill of quantities to be done (hereinafter called the contract or works as per drawings and specifications.

AND WHEREAS the said drawings and the specifications and priced schedule of quantities and other documents forming part of this contract have been signed by or on behalf of the parties hereto.

AND WHEREAS upon issue of tender for the works and receipt of the same duly filled in from the Contractor and upon further discussions held since receipt of the tender. The Owner had issued to the Contractor a letter of intent vide letter No. -------------------------------- dated ------------------------------------------  to mobilize and execute upon and subject to the conditions and instructions set forth herein (hereinafter referred to as the conditions) the works shown upon the said drawings and /or described in the specifications and included in the said Bill of Quantities at the item rate therein set forth hereinafter referred to as the Contract Price.

AND WHEREAS the Contractor has agreed to execution upon and abide by the conditions stipulated and complete the work.

NOW IT IS HEREBY AGREED AS FOLLOWS :

1.	In consideration of the said Contract Price to be paid at the times and in the manner set forth in the said conditions, the Contractor shall upon and subject to the said conditions, execute and complete the works shown upon the said drawings and described in the specifications and / or the priced Bill of Quantities.

2.	The Owner shall pay the Contractor the said Contract price or such other sum as shall become payable at the time and in the manner hereinafter specified in the said conditions.

3.	The said conditions and appendices thereto shall be read and construed as forming part of this agreement and the parties hereto shall respectively abide by and submit themselves to the conditions and perform the Agreement on their part respectively in such conditions contained.

4.	All disputes arising out of or in any way connected with this agreement shall be deemed to have arisen in Pune and only courts in Pune shall have jurisdiction to determine the same.

5.	This contract comprises:

- COVER SHEET

- INDEX

- TENDER NOTICE

- INSTRUCTIONS TO TENDERERS

- FORM OF TENDER

- APPENDIX TO FORM OF TENDER

- GENERAL CONDITIONS OF CONTRACT

- TECHNICAL SPECIFICATIONS

- BILL OF QUANTITIES

- PROFORMA FOR CONTRACT AGREEMENT  (Articles of Agreement)

- LIST OF APPROVED MAKES

6.	The Owner acting on his own or through the Architects reserves for itself the right of altering, adding, omitting or executing departmentally any items of works without prejudice to this contract.

7.	IN WITNESS WHEREOF the Contractor has caused their common seal to be hereunto affixed on the day, month and year first above written and the Owner has caused the same to be executed by the hand of Mr. ---------------------------  its Project Manager (Appointment) and authorized official as hereinafter appearing.

Signed on behalf of the Contractor common seal of the Contractor –

M/S.  ------------------------------------------

By the hand of Mr. -------------------------------------------

Authorised pursuant to the resolution of the Board of Directors of the Contractor,

Passed on their behalf on the ……………………………………..,

1.	……………………………………………………………….

2.	……………………………………………………………….

Signed on behalf of the IUCAA by the hand of Mr. E. M. Modak, Senior Administrative Officer, IUCAA in the presence of :

1.	……………………………………………………………….

2.	……………………………………………………………….